## SSO SUMMARY
The first two sections count the number of events and volume amounts for each type of Sanitary Sewer Overflow (SSO) for each municipality and in total | [23 empty] | This secion keeps track of the approximate gallons spilled from SSOs by municipality - a combined total of CSOs and SSOs is on the Reached Water Summary Tab
Municipality | # of SSO Events | # of NPDES Permitted Bypasses | # ot TOTAL EVENTS | All Events Total Estimated Gallons | # Reached Water | # Approved Bypass for Construction | Volume (gallons) Approved Bypass for Construction | # Excessive Flows - Storm Event | Volume (gallons) Excessive Flows - Storm Event | # Electrical Equipment Failure | Volume (gallons) Eletrical Equipt Failure | # Mechanical Equipment Failure | Volume (gallons) Mech Equipt Failure | # Other - Sewer Break | Volume (gallons) Other - Sewer Break | # Sewer Line Blockage - Grease | Volume (gallons) Line Blockage - Grease | # Sewer Line Blockage - Roots | Volume (gallons) Line Blockage - Roots | # Sewer Line Blockage - Other | Volume (gallons) Link Bolckage - Other | # Unknown Cause | Volume (gallons) Unknown Cause | Unnamed Waterbody (gallons) | CT River (gallons) | Farmington River (gallons) | East Swamp Brook (gallons) | Bridgeport Harbor (gallons) | Cedar Creek (gallons) | Ox Brook (gallons) | Still River (gallons) | Limekiln River (gallons) | Goodwives River (gallons) | Noroton River (gallons) | Long Island Sound (gallons) | Stonybrook River (gallons) | Housatonic River (gallons) | Succor Brook (gallons) | Ash Creek (gallons) | Turney Creek (gallons) | Rooster River (gallons) | New Haven Harbor (gallons) | Brothers Brook (gallons) | Birch Plain Creek (gallons) | Pequonnock River (gallons) | Pomperaug River (gallons) | Transylvania Brook (gallons) | Quinnibaug River (gallons) | Folly Brook (gallons) | Piper Brook (gallons) | Trout Brook (gallons) | Webster Brook (gallons) | Park River (incl N, S & Conduit) (gallons) | Hockanum River (gallons) | Quinnipiac River (gallons) | Meetinghouse Brook (gallons) | Beaverbrook Trail (gallons) | Naugatuck River (gallons) | Filling Hill Brook (gallons) | Beacon Hill Brook (gallons) | Willow Brook (gallons) | Bentley Creek (gallons) | Pootatuck River (gallons) | Byram Harbor (gallons) | Byram River (gallons) | Greenwich Harbor (gallons) | Horseneck Brook (gallons) | Indian Harbor (gallons) | Keeler Brook (gallons) | Norwalk River (gallons) | Ford Brook (gallons) | Yantic River (gallons) | Thames River (gallons) | Shetucket River (gallons) | Little River (gallons) | Horse Brook (gallons) | Moosup River (gallons) | Great Swamp (gallons) | Scantic River (gallons) | Avery Brook (gallons) | Willimantic (gallons) | Rippowam River (gallons) | Stamford Harbor (gallons) | Fisher's Island Sound (gallons) | Bruce Brook (gallons) | Mad River (gallons) | Cove River (gallons) | Oyster River (gallons) | West River (gallons)
Ansonia | 4 | 0 | 4 | 50 | 0 | [12 empty] | 1 | 5 | 3 | 45
Bethel | 1 | 0 | 1 | 50 | 1 | [12 empty] | 1 | 50 | 0 | [6 empty] | 50
Bloomfield (MDC) | 2 | 0 | 2 | 31 | 0 | [12 empty] | 1 | 30 | 1 | 1
Branford | 5 | 0 | 5 | 1300 | 0 | 2 | 0 | [12 empty] | 3 | 1300
Bridgeport (East & West) | 1 | 26 | 27 | 304910520 | 27 |  |  | 26 | 304910000 | [6 empty] | 1 | 520 |  |  | 0 | [7 empty] | 224400000 | 80510000 | 520
Bristol | 5 | 0 | 5 | 1300 | 3 |  |  | 3 | 300 | [6 empty] | 1 | 700 |  |  | 1 | 300 |  |  | 850
Cheshire | 1 | 0 | 1 | 700 | 1 | [14 empty] | 1 | 700 |  |  | 700
Cromwell (Mattabassett) | 3 | 0 | 3 | 75805000 | 2 |  |  | 3 | 75805000 | [15 empty] | 75730000
Danbury | 6 | 0 | 6 | 1004200 | 2 |  |  | 2 | 1003000 |  |  | 1 | 300 |  |  | 2 | 600 |  |  | 1 | 300 | [9 empty] | 3000 | 1000000
Darien | 15 | 0 | 15 | 27529 | 15 |  |  | 14 | 27454 |  |  |  |  | 1 | 75 | [17 empty] | 4523 | 125 | 21361 | 1520
Derby | 4 | 0 | 4 | 10630 | 1 |  |  | 3 | 10600 | [12 empty] | 1 | 30 | [13 empty] | 3000 | 5000
East Haddam | 1 | 0 | 1 | 5000 | 1 | [8 empty] | 1 | 5000
East Hampton | 2 | 0 | 2 | 31000 | 0 | [6 empty] | 2 | 31000
East Hartford (MDC) | 5 | 0 | 5 | 4065 | 1 |  |  | 1 | 3000 | [6 empty] | 2 | 960 |  |  | 1 | 100 | 1 | 5 | [30 empty] | 950
East Haven (GNHWPCA) | 2 | 0 | 2 | 30 | 0 | 1 | 0 | [8 empty] | 1 | 30
East Windsor | 2 | 0 | 2 | 0 | 0 | 1 | 0 | [8 empty] | 1 | 0
Enfield | 1 | 0 | 1 | 500000 | 1 |  |  | 1 | 500000 | [15 empty] | 500000
Fairfield | 8 | 0 | 8 | 210183 | 5 |  |  | 4 | 210000 | [6 empty] | 1 | 3 | 1 | 50 | 2 | 130 | [17 empty] | 135000 | 75000 | 50
Farmington | 1 | 0 | 1 | 30000 | 0 | [6 empty] | 1 | 30000
Greenwich | 36 | 0 | 36 | 17100 | 32 |  |  | 34 | 16550 |  |  | 1 | 500 | [8 empty] | 1 | 50 | [11 empty] | 3200 | [7 empty] | 500 | [20 empty] | 600 | 1350 | 8300 | 2600 | 300
Groton (City, Town & USN) | 10 | 0 | 10 | 3795 | 2 |  |  | 1 | 100 | 1 | 300 | 1 | 100 |  |  | 6 | 3195 |  |  |  |  | 1 | 100 | [20 empty] | 3000 | 100
Griswold (Jewett City) | 2 | 0 | 2 | 9300 | 1 |  |  | 1 | 9000 | [8 empty] | 1 | 300 | [28 empty] | 9000
Hamden (GNHWPCA) | 1 | 0 | 1 | 30 | 0 | [14 empty] | 1 | 30
Hartford (MDC) | 9 | 0 | 9 | 468900 | 6 | [6 empty] | 2 | 12000 | 1 | 69000 |  |  |  |  | 2 | 371000 | 4 | 16900 |  | 23000 | [27 empty] | 443000
Lebanon | 1 | 0 | 1 | 30 | 0 | [14 empty] | 1 | 30
Litchfield | 1 | 0 | 1 | 0 | 0 |  |  |  |  | 1 | 0
Manchester | 6 | 0 | 6 | 2003830 | 5 |  |  | 1 | 1000000 | 1 | 1000000 | 2 | 530 |  |  | 2 | 3300 | [31 empty] | 3000 |  |  |  |  | 2000530
Mansfield (UCONN) | 6 | 0 | 6 | 1140 | 0 |  |  | 3 | 900 |  |  | 1 | 0 | 1 | 0 | [6 empty] | 1 | 240
Meriden | 7 | 0 | 7 | 3380800 | 3 |  |  | 2 | 3380000 |  |  | 1 | 700 |  |  | 2 | 50 |  |  | 2 | 50 | [33 empty] | 3380000 | 700
Middletown | 10 | 0 | 10 | 2530 | 4 |  |  | 3 | 2150 | [6 empty] | 1 | 60 | 3 | 140 | 3 | 180 |  |  |  | 2300
Milford | 7 | 0 | 7 | 33495 | 3 |  |  | 3 | 33030 |  |  | 1 | 30 | [6 empty] | 2 | 60 | 1 | 375 | [11 empty] | 3000 |  | 30 | [19 empty] | 30000
Montville | 2 | 0 | 2 | 76000 | 1 |  |  | 1 | 75000 |  |  | 1 | 1000 | [59 empty] | 75000
Naugatuck | 5 | 0 | 5 | 86475 | 3 |  |  | 1 | 84000 | 1 | 1500 | [6 empty] | 1 | 75 | 2 | 900 | [36 empty] | 1500 | 750 | 84000
New Britain | 17 | 0 | 17 | 2450 | 16 |  |  | 17 | 2450 | [40 empty] | 600 |  | 1500 | [8 empty] | 300
New Haven (GNHWPCA) | 28 | 0 | 28 | 26506071 | 8 |  |  | 8 | 26500000 |  |  | 1 | 3000 |  |  | 12 | 2581 | 2 | 275 | 2 | 150 | 3 | 65 | [18 empty] | 26503000
New London | 2 | 0 | 2 | 1000100 | 1 |  |  | 1 | 1000000 | [6 empty] | 1 | 100 | [44 empty] | 1000000
New Milford | 1 | 0 | 1 | 300 | 1 | [10 empty] | 1 | 300 | [19 empty] | 300
Newington (MDC) | 7 | 0 | 7 | 586060 | 2 | 1 | 0 | 2 | 585860 | [12 empty] | 4 | 200 | [28 empty] | 585860
Newtown | 1 | 0 | 1 | 300 | 1 | [14 empty] | 1 | 300 | [41 empty] | 300
North Haven | 6 | 0 | 6 | 4003975 | 3 |  |  | 2 | 4000000 | [6 empty] | 3 | 3825 |  |  | 1 | 150 |  |  | 3000 | [30 empty] | 1300000
Norwalk | 20 | 4 | 24 | 3304355 | 8 |  |  | 4 | 3300000 | 1 | 30 | 4 | 660 |  |  | 4 | 1700 | 1 | 50 | 8 | 1855 | 2 | 60 | [45 empty] | 1400 | 3300030
Norwich | 26 | 0 | 26 | 536844 | 0 |  |  | 1 | 24000 |  |  | 8 | 327366 |  |  | 2 | 180 | 1 | 6000 | 8 | 32905 | 6 | 146393 | [47 empty] | 24780 | 71100 | 402814 | 6850
Orange | 1 | 0 | 1 | 12118 | 1 | [16 empty] | 1 | 12118 | 12118
Oxford | 1 | 0 | 1 | 12500 | 1 | [8 empty] | 1 | 12500 | [59 empty] | 12500
Plainfield | 8 | 0 | 8 | 340985 | 2 | [6 empty] | 6 | 340675 | [6 empty] | 2 | 310 | [54 empty] | 30000 | 300
Plymouth | 4 | 0 | 4 | 465 | 2 | [6 empty] | 1 | 5 | [6 empty] | 1 | 300 | 2 | 160 | 450
Putnam | 4 | 0 | 4 | 150 | 0 | [6 empty] | 1 | 0 |  |  | 1 | 50 | 1 | 50 | 1 | 50
Ridgefield | 2 | 0 | 2 | 250030 | 1 |  |  | 1 | 250000 | [6 empty] | 1 | 30 | [60 empty] | 250000
Rocky Hill (MDC) | 1 | 0 | 1 | 150 | 1 | [6 empty] | 1 | 150 | [11 empty] | 150
Seymour | 1 | 0 | 1 | 30 | 0 | [10 empty] | 1 | 30
Shelton | 2 | 0 | 2 | 60 | 0 | [14 empty] | 2 | 60
Simsbury | 2 | 0 | 2 | 60 | 0 |  |  | 1 | 30 | [10 empty] | 1 | 30
Somers | 1 | 0 | 1 | 10000 | 1 | [6 empty] | 1 | 10000 | [65 empty] | 10000
South Windsor | 9 | 0 | 9 | 180700 | 6 |  |  | 1 | 3000 | 5 | 176000 | 2 | 1550 | [8 empty] | 1 | 150 | 50 | 126000 | [54 empty] | 50000
Southbury (Heritage Village) | 2 | 0 | 2 | 2800 | 2 | [6 empty] | 1 | 100 | [8 empty] | 1 | 2700 | [22 empty] | 100 | 2500
Southington | 6 | 0 | 6 | 3420 | 1 |  |  | 1 | 3000 | [6 empty] | 5 | 420 | [37 empty] | 3000
Stafford | 2 | 0 | 2 | 3750 | 1 |  |  | 1 | 3000 | [10 empty] | 1 | 750 | [59 empty] | 3000
Stamford | 11 | 0 | 11 | 1048140 | 6 |  |  | 4 | 1000810 |  |  | 2 | 13000 | 1 | 25200 | 2 | 100 |  |  | 1 | 30 | 1 | 9000 | [11 empty] | 750 | [46 empty] | 30 | 1022000
Stonington | 2 | 0 | 2 | 1300 | 1 |  |  |  |  | 1 | 1000 | [8 empty] | 1 | 300 | [62 empty] | 1000
Stratford | 7 | 0 | 7 | 27738300 | 6 |  |  | 5 | 27728000 | 1 | 10000 | [8 empty] | 1 | 300 | [15 empty] | 27737800 | [47 empty] | 300
Suffield | 4 | 0 | 4 | 660 | 0 |  |  | 1 | 300 |  |  | 2 | 60 |  |  | 1 | 300
Thomaston | 1 | 0 | 1 | 5000 | 1 |  |  | 1 | 5000 | [48 empty] | 5000
Torrington | 3 | 0 | 3 | 610 | 2 |  |  | 2 | 600 | [10 empty] | 1 | 10 | [36 empty] | 610
Trumbull | 1 | 0 | 1 | 300 | 0 | [10 empty] | 1 | 300
Vernon | 3 | 0 | 3 | 3000000 | 3 |  |  | 3 | 3000000 | [44 empty] | 3000000
Wallingford | 4 | 0 | 4 | 2033000 | 2 |  |  | 4 | 2033000 | [45 empty] | 2000000
Waterbury | 14 | 1 | 15 | 1010451 | 3 |  |  | 2 | 1000750 | [6 empty] | 1 | 100 | 1 | 20 | 6 | 9441 | 5 | 140 | [34 empty] | 1000000 | [27 empty] | 5350
Waterford | 2 | 0 | 2 | 600 | 0 | [6 empty] | 1 | 300 | [6 empty] | 1 | 300
West Haven | 27 | 0 | 27 | 1062365 | 11 |  |  | 8 | 1062000 |  |  | 1 | 20 |  |  | 11 | 205 | 1 | 20 | 5 | 100 | 1 | 20 | 20 | [10 empty] | 30000 | [6 empty] | 1002000 | [44 empty] | 10000 | 10000 | 10040
West Hartford (MDC) | 32 | 0 | 32 | 87824275 | 29 |  |  | 29 | 87824000 | [6 empty] | 1 | 150 | 1 | 75 |  |  | 1 | 50 | 150 | [25 empty] | 55896000 | 23310000
Westport | 1 | 0 | 1 | 3000 | 0 |  |  | 1 | 3000
Wethersfield (MDC) | 2 | 0 | 2 | 1050 | 1 |  |  | 1 | 1000 | [12 empty] | 1 | 50 | 1000
Windsor (MDC) | 2 | 0 | 2 | 379000 | 1 |  |  | 1 | 378000 | [10 empty] | 1 | 1000 |  |  |  |  | 378000
Windsor Locks | 1 | 0 | 1 | 150 | 1 | [14 empty] | 1 | 150 |  |  |  | 150
SUMMARY | 443 | 31 | 474 | 549490887 | 246 | 5 | 0 | 209 | 546777884 | 12 | 1188830 | 46 | 773046 | 6 | 111775 | 68 | 19789 | 17 | 7140 | 72 | 423617 | 39 | 188806
Data Caveats
While DEEP is the storehouse for the SRTK data, DEEP makes the following caveats:
· All data is submitted by publicly owned wastewater treatment plants and publicly owned satellite collection systems.
· DEEP does not issue notifications about individual discharges, they are inputted by the reporters for each municipality and issued by the electronic system automatically.
· The reports are being submitted by the municipalities in a short time frame after discovery of a discharge and specific details may not be known.
· Data is estimated based on the existing systems, models, and personal knowledge of the sewer systems by the reporters.
· Data quality, especially volumes, is not checked by DEEP.
· The electronic program allows for zero duration, short durations and zero quantities for volumes.
· Addresses may not be entered by municipalities in a way that allows the parts of the address to be separated nor with an exact location.
· Multiple notifications may be sent for the same discharge since municipalities need to submit daily and termination reports for ongoing discharges.
· Duplicate reports and reports submitted that resulted in zero flow may be rescinded in the system.

## ANSONIA
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Ansonia | Ansonia | Glen Drive | Sewage Bypass | Dry | 11/30/2021, 11:53 AM | 12/2/2021, 10:30 AM | Pump Station | No | Raw Sewage | Sewer Line Blockage - Other |  | 1-50 gallons | O&M manual |  | 25 | No | Mechanical byass for repairs
Ansonia | Ansonia | liberty Street | Sewage Bypass | Dry | 3/1/2021, 1:00 PM | 3/1/2021, 1:30 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | resident called in | 1-50 gallons | estimate |  | 5 | No
Ansonia | Ansonia | Coe lane Ansonia, CT. 06401 | Sewage Bypass | Dry | 6/15/2021, 8:15 AM | 6/15/2021, 2:30 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | Small crack was seeping on road | 1-50 gallons | estimate |  | 15 | No | Mechanical byass for repairs
Ansonia | Ansonia | Wakelee Ave Ansonia CT. 06401 | Sewage Bypass | null | 6/7/2021, 10:26 AM | 6/8/2021, 9:00 AM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Roots | resident called | 1-50 gallons | estimate |  | 5 | No

## BETHEL
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Bethel | Bethel | Whittlesey Dr | Sewage Bypass | Dry | 3/20/2021, 3:30 PM | 3/20/2021, 5:30 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Roots | Phone call | Undetermined | N/A | N/A | 50 | Yes | East Swamp Brook | Roots were removed to clear blockage in sewer pipe.

## BRANFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Branford | Branford | 75 Block Island Rd | Approved Bypass for Constrution Projects | Dry | 4/20/2021, 7:57 AM | 4/22/2021, 10:15 AM | Pump Station | No | Raw Sewage | Approved Bypass for Construction |  | 0 |  |  | 0 | No |  | the Force main at Bradley pump Station located at 50 Bradley ave Branford CT is being changed out.
Branford | Branford | 50 Bradley Ave | Approved Bypass for Constrution Projects | Dry | 5/17/2021, 1:38 PM | 5/18/2021, 10:15 AM | Pump Station | No | Raw Sewage | Approved Bypass for Construction |  | 0 |  |  | 0 | No |  | chaining out 10 foot section of force main at Bradley pump station and installing new flow meter.
Branford | Branford | Salt Meadow Lane | Sewage Bypass | Dry | 3/30/2021, 11:08 AM | 3/30/2021, S:35 PM | Pump Station | No | Raw Sewage | Sewer Line Blockage - Other | Pump Station crew noticed one of the two force main lines in wet well was broke | 51 - 500 gallons | visual |  | 300 | No |  | Linden Shores Pump Station located at 26 Linden Shores , one of the 4 inch force mains from the wet well to the valve pit five feet away broke and needs to be replaced. the other 4 inch force main from wet well to valve pit will be replaced too.
Branford | Branford | 116 Maple St | Sewage Bypass | Dry | 4/16/2021, 6:26 PM | 4/16/2021, 8:30 PM | Sewer Main | No | None | Sewer Line Blockage - Other | Police department called on call phone | 501 - 1,000 gallons | Visual |  | 700 | No |  | Force Main broke. the pump station was shut off and the flow to station was diverted to other station due to valve that lets flow to maple pump station to be diverted .
Branford | Branford | 383 East Main Street Branford | Sewage Bypass | null | 7/13/2021, 10:17 AM | 7/13/2021, 3:15 PM | Pump Station | No | None | Sewer Line Blockage - Other | 8 Inch force main broke | 51 - 500 gallons | visual estimate |  | 300 | No |  | there are two force main lines that come from the Route 139 pump station, one line is 8 inch the other line is 12 inch the 8 inch line broke around 70 feet from pump station. the 8 inch force main valve is shut off the station is using the 12 inch line.

## BRIDGEPORT
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Bridgeport – Collection System | Bridgeport | 55 Stoehrs Place | Sewage Bypass | Other | 9/2/2021, 9:50 AM | 9/2/2021, 10:22 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Resident called WPCA of overflow condition | 501 - 1,000 gallons | Visually estimated | Approximately 520 gallons | 520 | Yes | Ox brook
Bridgeport Eastside | Bridgeport | 695 Seaview Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 10/26/2021, 9:00 AM | 10/26/2021, 2:00 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operations observing flow meter and pumping rates | 500,001 - 999,999 gallons | Flow Meter Totalizer | 2.71 mg | 2710000 | Yes | Bridgeport Harbor
Bridgeport Eastside | Bridgeport | 695 Seaview Ave | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 2/16/2021, 6:15 AM | 2/16/2021, 9:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics Street level indicator | Undetermined | Miltronics Street level indicator | 1.47 mg | 1470000 | Yes | Bridgeport Harbor, Long Island Sound
Bridgeport Eastside | Bridgeport | 695 Seaview Ave | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 4/15/2021, 6:00 PM | 4/15/2021, 8:45 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics-Street Level Indicator | Undetermined | Miltronics- Street level indicator | 1.42mg | 1420000 | Yes | Bridgeport Harbor - Long Island Sound | Rainfall 1.33"
Bridgeport Eastside | Bridgeport | 695 seaview Avenue, Bridgeport, CT 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 5/28/2021, 10:30 PM | 5/29/2021, 04:30 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics street level indicator | Over 1,000,000 gallons | Milltronics flow totalizer | 0.94 | 940000 | Yes | Bridgeport Harbor | Two bypasses through the night
Bridgeport Eastside | Bridgeport | 695 Seaview Avenue, Bridgeport, Ct 06607 | NPDES Permitted Bypass of Secondary Treatment | null | 5/4/2021, 2:30 AM | 5/4/2021, 5:30 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics street level meter | Over 1,000,000 gallons | Milltronic flow totalizer | 1.32 | 1320000 | Yes | Bridgeport Harbor | 0.90 inches of rainfall
Bridgeport Eastside | Bridgeport | 695 Seaview Avenue, Bridgeport, CT 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 7/1/2021, 10:30 PM | 7/2/2021, 1:30 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics street level meter | Undetermined | Milltronics flow totalizer | 1.16 mg | 1160000 | Yes | Bridgeport Harbor | 1.5 inches of rainfall. Cl2 was 0.03
Bridgeport Eastside | Bridgeport | 695 Seaview Avenue, Bridgeport, Connecticut 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 7/8/2021, 5:00 PM | 7/8/2021, 8:00 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics Street Level Indicator | Undetermined | Milltronics Flow Totalizer | 1.55 | 1550000 | Yes | Bridgeport Harbor | 0.90 inches of rain. Cl2 residual was 0.03
Bridgeport Eastside | Bridgeport | 695 seaview Avenue, Bridgeport, Connecticut 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 7/9/2021, 6:00 AM | 7/9/2021, 2:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics street level meter | Undetermined | Milltronics flow totalizer | 4.56 MG | 4560000 | Yes | Bridgeport Harbor | 3.63 Inches of rainfall. Cl2 residual was 0.05
Bridgeport Eastside | Bridgeport | 695 seaview Avenue, Bridgeport, CT 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 8/23/2021, 9:40 AM | 8/23/2021, 1:15 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics Street Level Indicator | Undetermined | Milltronic Flow Totalizer | 1.80 MG | 1800000 | Yes | Bridgeport Harbor | 1.17 Inches of rain
Bridgeport Eastside | Bridgeport | 695 Seaview Avenue, Bridgeport, CT 06607 | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 9/1/2021, 9:30 PM | 9/2/2021, 10:00 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Milltronics Street level Indicator | Undetermined | Milltronics flow totalizer | 5.51 | 5510000 | Yes | Bridgeport Harbor
22440520
Bridgeport Westside | Bridgeport | 205 Bostwick Ave. | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 2/16/2021, 6:15 AM | 2/16/2021, 12:15 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics Street Level Indicator | Undetermined | Miltronics Street Level Indicator | 5.7mg | 5700000 | Yes | Cedar Creek Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 2/22/2021, 5:10 PM | 2/22/2021, 9:00 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics Street Level Indicator | Undetermined | Miltronics Street Level Indicator | 5.55mg | 5550000 | Yes | Cedar Creek / Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave. | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 2/27/2021, 12:15 PM | 2/27/2021, 4:30 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics Street Level Indicator | Undetermined | Miltronics Street Level Indicator | 2.92mg. | 2920000 | Yes | Cedar Creek / Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Avenue Bridgeport CT 06605 | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 3/28/2021, 12:30 PM | 3/28/2021, 4:05 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operations observing flow meter | Undetermined |  |  | 3000000 | Yes | Cedar Creek
Bridgeport Westside | Bridgeport | 205 Bostwick Ave. | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 4/15/2021, 2:55 PM | 4/16/2021, 1:00 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltronics- Street Level Indicator | Undetermined | Miltronics- Street Level Indicator | 6.42mg | 6420000 | Yes | Cedar Creek- Long Island Sound | Rainfall 1.31"
Bridgeport Westside | Bridgeport | 205 Bostwick Avenue Bridgeport CT 06605 | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 4/25/2021, 11:05 AM | 4/25/2021, 12:45 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | operators observing flow meter | Undetermined | Flow meter totalizer | 0.98 MG | 980000 | Yes | cedar creek
Bridgeport Westside | Bridgeport | 205 Bostwick Ave. | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 5/28/2021, 10:13 PM | 5/29/2021, 6:30 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Miltonic's street level indicator | Undetermined | Miltonic's street level indicator | 11.07mg. | 11070000 | Yes | Cedar Creek / Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Avenue Bridgeport CT 06605 | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 5/4/2021, 2:00 AM | 5/4/2021, 7:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operations monitoring influent flow meter | Undetermined | Flow Meter Totalizer | 3.27 | 3270000 | Yes | Cedar Creek
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 7/2/2021, 8:30 PM | 7/3/2021, 2:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Visual observation | Undetermined |  |  | 3000000 | Yes | Cedar Creek / Long Island sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 7/29/2021, 6:55 PM | 7/29/2021, 11:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Visual observation | Undetermined |  | 2.39 | 2390000 | Yes | Cedar Creek / Long Island sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 7/8/2021, 5:44 PM | 7/8/2021, 11:35 PM | Treatment Plant | Unknown at this time | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Visual observation | Undetermined |  |  | 3000000 | Yes | Cedar Creek/Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 7/9/2021, 6:25 AM | 7/9/2021, 10:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Visual observations | Undetermined |  |  | 3000000 | Yes | Cedar Creek / Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 8/22/2021, 10:25 AM | 8/22/2021, 1:25 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator Observation | Undetermined | Flow Meter | 2.19 | 2190000 | Yes | Cedar Creek Long Island Sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 8/23/2021, 9:30 AM | 8/23/2021, 2:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Observation | Undetermined | Flow Meter | 3.92 | 3920000 | Yes | Cedar Creek Long Island Sound
Bridgeport Westside | Bridgeport | 203 Bostwick avenue | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 9/1/2021, 9:35 PM | 9/2/2021, 4:00 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Observation | Undetermined |  | 20.96 | 20960000 | Yes | Cedar Creek Long Island sound
Bridgeport Westside | Bridgeport | 205 Bostwick Ave. | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 9/24/2021, 9:00 AM | 9/24/2021, 12:30 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | milltronics street level indicator | Undetermined | milltronics street level indicator | 3.14mg. | 3140000 | Yes | Cedar Creek - Long Island Sound | Close out report
80510000

## BRISTOL
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Bristol WPCA | Bristol | Stevens Street | Sewage Bypass | Dry | 1/3/2021, 12:00 PM | 1/3/2021, 2:15 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Resident discovered while walking St Paul Sewer cross lot | 501 - 1,000 gallons | Based of amount discharging upon arrival and time called in. Cross lot is walked frequently by residents. Believed bypass was discovered shortly after it started. | unknown | 700 | Yes | New Britian water shed
Bristol WPCA | Bristol | 240 Burlington Avenue | Sewage Bypass | Dry | 5/18/2021, 9:55 AM | 5/18/2021, 11:00 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | Received call from Bristol Fire Department that sewage was backing up into unit 29 at 240 Burlington Avenue | 51 - 500 gallons | Estimated |  | 300 | No
Bristol WPCA | Bristol | Jewel Street | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 11:11 AM | 9/2/2021, 11:11 AM | Lateral - Private | Yes | Raw Sewage | Excessive Flows - Storm Event | Recieved calls from 6 different homeowners in close proximaty. main sewer line surcharged do to storm event. bypassed into multiple houses. | Undetermined |  |  | 150 | No |  | Do to Ida tropical storm event, sewer cross lot became surcharged causing main sewer line to back up on Stafford avenue impacting multiple resident on Charles, Jewel and Duncan street as well as Milton Road. Total of 6 homeowner have reported sewage in basement.
Bristol WPCA | Bristol | South Street | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 11:26 AM | 9/2/2021, 4:25 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | discovered during visual inspection of memorial boulevard | Undetermined |  |  | 50 | Yes | City of Bristol, detension pond | Main sewer line in the grass between Memorial Boulevard and South Street bypassed into the grass and drained into downstream detention pond.
Bristol WPCA | Bristol | 75 Battista Rd Bristol CT 06010 | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 2:30 AM | 9/2/2021, 3:30 AM | Treatment Plant | No | Raw Sewage | Excessive Flows - Storm Event | Operator noticed flow coming over channel near Primary Gallery | Undetermined | Unknown |  | 100 | Yes | Unknown, overflow went into the facilities storm basin system. | Issue at Broad Street Pump Station required 4 pumps to be turned on to pump it down. With 4 pumps online and the flow being up from the rain, the channel by the Primary Clarifier was overflowing. Put another Primary Clarifier online and issue was resolved.
1300

## CHESHIRE
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Cheshire | Cheshire | East mitchell rd cheshire ct 06410 | Sewage Bypass | Dry | 2/6/2021, 9:00 PM | 2/8/2021, 12:00 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | reported by resident to police, who in turn contacted superintendent | 501 - 1,000 gallons | duration of overflow and estimated flow through the line |  | 700 | Yes | local stream of unknown name

## DANBURY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Danbury WPCF | Danbury | 79 Cross st | Sewage Bypass | Dry | 1/8/2021, 9:00 AM | 1/8/2021, 9:20 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Found surging by Sewer Crew | 51 - 500 gallons | Visual Estimate |  | 300 | No
Danbury WPCF | Danbury | 22 Lakeview Dr | Sewage Bypass | Other | 2/24/2021, 11:00 AM | 2/23/2021, 1:41 PM | Lateral - Private | No | Raw Sewage | Unknown | property owner called office | 0 | estimated | 0 | 0 | No |  | Bypass caused by a broken sewer lateral underground. | Not a bypass by definition - happened on private proeprty and was not caused by Danbury collection system
Danbury WPCF | Danbury | 170 Shelter Rock Rd Danbury CT 06810 | Sewage Bypass | Dry | 6/20/2021, 12:30 PM | 6/20/2021, 1:00 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Called in by resident | 51 - 500 gallons | visual | NA | 300 | No | N/A
Danbury WPCF | Danbury | 4 topstone drive Danbury CT 06810 | Sewage Bypass | Dry | 6/21/2021, 4:45 PM | 6/21/2021, 4:00 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Called in by resident | 51 - 500 gallons | visual | n/a | 300 | No | n/a
Danbury WPCF | Danbury | 10 Plumtrees Road, Danbury, CT 06810 | Sewage Bypass | Dry | 8/4/2021, 6:00 AM | 8/4/2021, 6:05 AM | Treatment Plant | No | Sludge Spill | Mechanical Equipment Failure | Operator On Duty | 51 - 500 gallons | Estimated based on duration of bypass |  | 300 | No |  | Suction hose dislodged from a trash pump causing sludge to syphon from a gravity thickener tank onto the roadway within the treatment plant. Problem was corrected within 5 minutes by operator on duty. Spill has been cleaned up.
Danbury WPCF | Danbury | 2 National Place | Sewage Bypass | Rain > 4" per hour | 9/1/2021, 11:30 PM | 9/2/2021, 11:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Visual Inspection | 1,001 - 5,000 gallons | Visual Estimate |  | 3000 | Yes | Still River | During Storm IDA excessive flows and flooding waters caused the siphon at this location which goes under the Still River to exceed its capacity
Danbury WPCF | Danbury | Plumtrees Road | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 11:14 AM | 9/2/2021, 11:14 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator On Duty | Over 1,000,000 gallons | Bypassed flow (GPM) X Duration of Bypass |  | 1000000 | Yes | Limekiln Brook | Remnants from Hurricane IDA resulted in heavy flows for approximately 10 hours causing the wet weather flow equalization tank to fill by 6:30 am and start bypassing primary treated sewage directly to the chlorine contact tanks where it was disinfected and discharged to the receiving stream.
1004200

## DARIEN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Darien | Darien | West ave and Baily | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 2:43 PM | 7/9/2021, 4:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observations | 51 - 500 gallons | estimate of flow rate of weeping mh | 488 | Yes | goodwives river | on going
Darien | Darien | Brush Island Road | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 2:50 PM | 7/10/2021, 7:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Visual observation | 1,001 - 5,000 gallons | estimated flowrate | 8820 | Yes | Long Island Sound | on going,elg
Darien | Darien | Brushy Island Road | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 2:53 PM | 7/10/2021, 7:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 1,001 - 5,000 gallons | estimate of flowrate | 7575 | Yes | Long Island Sound | on going, elg
Darien | Darien | Brushy Island Road | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 2:56 PM | 7/10/2021, 7:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 51 - 500 gallons | estimated flow | 758 | Yes | Long Island Sound | on going
Darien | Darien | Sedgwick Avenue | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 2:59 PM | 7/9/2021, 10:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 51 - 500 gallons | estimated flow | 2535 | Yes | Goodwives River | on going
Darien | Darien | Post Rd | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 3:08 PM | 7/9/2021, 6:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 51 - 500 gallons | estimated flowrate | 1470 | Yes | Stony Brook River | on going
Darien | Darien | 42 Beach dr | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 3:13 PM | 7/10/2021, 2:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual estimate | 1-50 gallons | estimated flowrate | 2340 | Yes | Long Island Sound | on going
Darien | Darien | 26 Park Place | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 4:00 PM | 7/9/2021, 6:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation by area resident | 1-50 gallons | WAG. Report from resident. bypass was over when it was reported | 50 | Yes | Norton River | Area cleaned on morning of 7/10/21
Darien | Darien | Post Rd | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 4:42 PM | 7/9/2021, 7:15 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 1-50 gallons | estimated flowrate | 113 | Yes | Long Island Sound | on going
Darien | Darien | 23 Crimmins | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 4:45 PM | 7/9/2021, 4:48 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | visual observation | 1-50 gallons | estimated flowrate | 50 | Yes | Stony Brook River | stopped - not ongoing
Darien | Darien | 379 West Ave Darien, Ct | Sewage Bypass | Dry | 8/10/2021, 5:30 PM | 8/10/2021, 6:45 PM | Sewer Main | null | Raw Sewage | Other - Sewer Break | During a spot repair of a cracked sewer main. | 51 - 500 gallons | Visual observation/estimation | 75 | Yes | Noroton River (1500 LF downstream) | Experienced a loss of sewage during the repair of a cracked pipe.
Darien | Darien | 150 Nearwater Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 10:05 AM | 9/2/2021, 12:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | observation | 51 - 500 gallons | estimated | 945 | Yes | Long Island Sound | stopped
Darien | Darien | Old Kings Highway South at Sedgwick Avenue | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 10:08 AM | 9/2/2021, 12:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | observation | 1,001 - 5,000 gallons | estimated | 1500 | Yes | Goodwives River | on going
Darien | Darien | 90 Nearwater Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 9:44 AM | 9/2/2021, 12:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | observation | 51 - 500 gallons | estimated | 135 | Yes | Long Island Sound | stopped
Darien | Darien | 141 Nearwater Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 9:55 AM | 9/2/2021, 12:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | observation | 51 - 500 gallons | estimate | 675 | Yes | Long Island Sound | stopped
27529

## DERBY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Derby | Derby | 19 Cherry st | Sewage Bypass | Dry | 10/10/2021, 10:15 AM | 10/10/2021, 12:01 PM | Lateral - Private | No | Raw Sewage | Unknown | Derby PD reported a sewage leak to Derby PW, Derby PW contacted Derby WPCA | Undetermined | active bypass |  | 0 | Yes | Housatonic River | This is a private home lateral leak coming from 19 Cherry st Derby, Derby's sewer lines were inspected on Cherry and Summit st and lines are fine at this time, CT DEEP Emergency response was called at 11:37 am ( 860-424-3338 ) spoke with Agent #201 and reported sewage from a private home was discharging into a catch basin on the corner of Summit and cherry st. At 11:50 I received a call from Donnell with CT DEEP and explained the situation Donnell is going to 19 Cherry st to advise homeowner. | Not a bypass by definition - happened on private proeprty and was not caused by Danbury collection system
Derby | Derby | 8th street Derby, ct 06418 | Sewage Bypass | Dry | 3/16/2021, 12:36 PM | 3/22/2021, 10:00 AM | Lateral - Private | No | Raw Sewage | Unknown | call from resident | 1-50 gallons | Estimate, visual |  | 30 | No |  | Thursday March 11th, Upstream and downstream manholes of 109 Hawkins St, Derby were checked for a blockage after water was found around a sinkhole in the middle of the street our sewer main was running fine no blockages, also no evidence of sewage at that time, Naugatuck Valley health Dept. was called and Rich from NVH came to check out problem, Homeowner was called Friday March 12th at 4:18pm and assured the city that the lateral was cleaned it had root intrusion and wipes.
Derby | Derby | 1 caroline street derby ct | Sewage Bypass | Rain 3-4" per hour | 7/9/2021, 9:00 AM | 7/9/2021, 9:00 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | visual | Undetermined |  |  | 3000 | Yes | Housatonic river | Tropical Storm
Derby | Derby | Factory st | Sewage Bypass | Rain 2-3" per hour | 8/23/2021, 10:30 AM | 8/23/2021, 12:19 PM | Treatment Plant | No | Raw Sewage | Excessive Flows - Storm Event | Plant Operator reported overflow | 1,001 - 5,000 gallons | estimate | unknown | 3000 | No |  | High flow rain event causing Grit chamber overflow.
Derby | Derby | Caroline St | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 4:30 AM | 9/2/2021, 6:20 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | plant walk around | 5,001 - 20,000 gallons | Estimate, visual |  | 10000 | No |  | Excessive rain caused excessive flows to the plant along with Stevenson dam releasing 2500 CFS causing plant to backup and Clarifiers to flow over weirs. Raw sewage was also going down stairs to Grit chamber.
16030

## EAST HADDAM
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
East Haddam WPCF | East Haddam | 2 Norwich Rd East Haddam | Sewage Bypass | Dry | 2/17/2021, 10:30 PM | 2/26/2021, 3:30 PM | Lateral - Public | Yes | Raw Sewage | Unknown | Odor Complaint | 1,001 - 5,000 gallons | SCADA | 5,000 gallons | Yes | Succor Brook | Jim Ventres is contacting CT DOT for locational information on suspect repair. Given dangerous location (narrow steep curve) and pending ice storm, excavation and repairs to be scheduled following storm.

## EAST HAMPTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Derby | Derby | 19 Cherry st | Sewage Bypass | Dry | 10/10/2021, 10:15 AM | 10/10/2021, 12:01 PM | Lateral - Private | No | Raw Sewage | Unknown | Derby PD reported a sewage leak to Derby PW, Derby PW contacted Derby WPCA | Undetermined | active bypass |  |  | Yes | Housatonic River | This is a private home lateral leak coming from 19 Cherry st Derby, Derby's sewer lines were inspected on Cherry and Summit st and lines are fine at this time, CT DEEP Emergency response was called at 11:37 am ( 860-424-3338 ) spoke with Agent #201 and reported sewage from a private home was discharging into a catch basin on the corner of Summit and cherry st. At 11:50 I received a call from Donnell with CT DEEP and explained the situation Donnell is going to 19 Cherry st to advise homeowner.
EAST HAMPTON WPCA | East Hampton | 124 Laurel Ridge, East Hampton, CT | Sewage Bypass | Dry | 12/19/2021, 11:45 AM | 12/19/2021, 12:15 PM | Sewer Main |  | Raw Sewage | Mechanical Equipment Failure | Police called sewer dispatch service | 1000 gallons | Estimate of pumping over time to shut down station to bypass. | 1000 gallons | 1000 | No |  | Pump shut off. Bypass with pumping until repairs completed.
East Hampton WPCA | East Hampton | Daly Rd, East Hampton, CT 06424 | Sewage Bypass | Other | 2/8/2021, 7:30 PM | 2/8/2021, 8:30 PM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | Pedestrian walking by sewer pipe | 20,001 - 50,000 gallons | Estimate |  | 30000 | No

## EAST WINDSOR
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
East Windsor WPCF | East Windsor | 192 South Water Street, East Windsor, CT | Approved Bypass for Constrution Projects | Dry | 4/28/2021, 8:08 AM | 4/28/2021, 12:10 PM | Treatment Plant | No | Raw Sewage | Approved Bypass for Construction | Scheduled Maintenance - Cleaning Final Contact Tank prior to disinfection season. | 0 | Not currently disinfecting, no issues with flow. | NA | No |  | Scheduled seasonal maintenance - normal procedure
East Windsor WPCF | Suffield | 136 Prospect Hill Rd, East Windsor, CT | Sewage Bypass | Dry | 4/23/2021, 10:28 AM | 4/23/2021, 4:30 PM | Sewer Main | Yes | Raw Sewage | Sewer Line Blockage - Grease | Local Restaurant was having some drain issues. | 0 | Line was partially plugged, nothing left manhole or mainline. | 0 | No | N/A | Restaurant was having some drain issues, a partial plug was discovered in the main sewer line. Line Cleaned, Jetted, Flushed. All normal.

## ENFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Enfield POTW | Enfield | 120 Prospect St Enfield | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 7:30 AM | 9/2/2021, 8:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Property owner saw what water coming out of the sanitary sewer cover | Undetermined | GPM by the hour | 500,000 gallons | Yes | CT River | Excessive rain causing the sanitary sewer system to over flow. Discharge was from SMH# 4800

## FAIRFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Fairfield WPCF | Fairfield | 637 Reef Road - exact location | Sewage Bypass | Dry | 1/29/2021, 10:00 AM | 1/29/2021, 10:15 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Called in by home owner | 1-50 gallons | Home owner said between 2 to 3 gallons over topped the toilet | 2 - 3 gallons. | 3 | No |  | Temperature in the teens grease, rags and roots clogged the line. We will camera the line to see what the inspection shows and take corrective action from there if any is needed.
Fairfield WPCF | Fairfield | 330 Richard White Way, Fairfield CT. 06516 | Sewage Bypass | Dry | 5/27/2021, 2:30 PM | 5/27/2021, 2:50 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other | Contractor hit and ripped off top of 8 inch sanitary line. When the top of pipe was ripped off dirt went into pipe and blocked line. | 1-50 gallons | Amount of water leaving pipe and duration, very little flow within line. | 30 Gallons | 30 | No |  | Some sewage escaped pipe when it was broken. Once dirt was removed from pipe water flowed within pipe and we used our water jet truck in the line upstream to act as a vacuum and pull water through. Very little flow in this line, hence the small amount of the bypass.
Fairfield WPCF | Fairfield | 330 One Rod Highway | Sewage Bypass | Dry | 6/9/2021, 9:55 AM | 6/9/2021, 12:00 PM | Treatment Plant | null | Sludge Spill | Sewer Line Blockage - Other | Contractor hit line while digging trench, reported to me as soon as it happened. | 51 - 500 gallons | Estimate |  | 100 | No |  | Contractor hit a 4" PVC scum line while digging . Plant personnel shut off scum pumps and drained scum pit back to plant headworks. The remaining water in the pipe leaked into the trench. Visual estimation of leak was reported . Water is to be tested, removed accordingly.
Fairfield WPCF | Fairfield | Hibiscus Ave, Berwick Ave, Grasmare Ave & Kings Highway & 2070 Kings Highway | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 12:24 PM | 7/9/2021, 11:45 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Staff inspection | Undetermined | Duration, flow pattern and height of water coming out of manholes | 20000 | 20000 | Yes | Ash Creek | Several manholes boiling out along East Trunk Line Interceptor.
Fairfield WPCF | Fairfield | Woodside Ave | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 3:15 PM | 7/9/2021, 6:30 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Called in by resident | Undetermined | Duration, flow pattern and height of water out of manhole | 7500 | 75000 | Yes | Turney Creek | Manhole overflowing
Fairfield WPCF | Fairfield | Brentwood & Kings Highway | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:28 AM | 7/9/2021, 6:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Staff checking locations | Undetermined | Duration, flow pattern and height of water coming out of manhole | 15000 | 15000 | Yes | Ash Creek | Effects from Tropical Storm Elsa, over 4 inches of rain from last night.
Fairfield WPCF | Fairfield | 350 Grace st | Sewage Bypass | Dry | 8/13/2021, 12:45 PM | 8/13/2021, 2:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Roots | called in by homeowner | 51 - 500 gallons | visual estimate | 250 gal | 50 | Yes | catch basin to rooster river | no solids were bypassed road was washed down of grey water.
Fairfield WPCF | Fairfield | 131 Royal Ave, 17, 138, 207 & 187 Rutland Ave, 114 Brentwood Ave, 75 Hibiscus Street, 124 & 178 Halley Ave, 119 Berwick Ave, 173, 253 & 291 Fairchild Ave, 39 Bradford Street, Dresden Street, 16 Carthage Street, 35 Kings Highway, 57 Pierce Street, Arising | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 12:30 AM | 9/2/2021, 11:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Staff visual inspection | Undetermined | Amount of manholes over flowing and duration. | 100000 | 100000 | Yes | Ash Creek, Rooster River | 35 manholes along the East Trunk line or overflowing due to heavy rains from Storm Ida flowing into the Rooster River & Ash Creek.
210183

## FARMINGTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Farmington | Farmington | 38 Patrick Flood Road Farmington CT | Sewage Bypass | Dry | 9/21/2021, 10:00 AM | 9/22/2021, 10:00 PM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | Operators saw sewage coming from crack in road, after troubleshooting discovered the force main had a break. | 20,001 - 50,000 gallons | Quantity was determined by pumping rates and time of break |  | No |  | The 14 inch force main out of the pump station broke, operators & contractors are currently digging up the road to find the break and will be replacing the broken section. Vac trucks are onsite vacc'ing the inflow to the pump station until work is finished.

## GNWPCA
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Greater New Haven WPCA | East Haven | 31 Commerce St East Haven CT 06512 | Approved Bypass for Constrution Projects | Dry | 1/25/2021, 2:00 PM | 1/28/2021, 2:00 PM | Sewer Main | No | Raw Sewage | Approved Bypass for Construction | scheduled lining of gravity main | 0 gallons | No sewage left the system | 0 gallons | 0 | No |  | lining of gravity main approx 600 LF of CIPP 24", lining scheduled to be completed after 2 days.
Greater New Haven WPCA | East Haven | 47 Moulthrup St East Haven Ct | Sewage Bypass | Dry | 4/6/2021, 2:30 PM | 4/6/2021, 3:24 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Called in by resident | 1-50 gallons | Field estimate by crew |  | 30 | No |  | Crew arrived and found sanitary sewer surcharged, line was blocked with grease and rags, line was cleared and flow restored. No bypasss in customers basement was reported but while jetting line sewerage came out of upstream manhole and ran into catch basin. road was washed off by crew and sewage was vacuumed out of catch basin.
Greater New Haven WPCA | Hamden | 597 Hamden Plaza and Mix Ave, Hamden, CT | Sewage Bypass | Dry | 12/22/2021, 02:15 PM | 12/22/2021, 02:45 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Rags | By-pass was reported by Hamden DPW. | Less than 50 gallons. | Field estimate by crew. The by-pass was not active when the crew arrived. | Less than 50 gallons. | 30 | No | N/A | When the crew arrived the by-pass was not active. The crew jetted the line and removed a driveway ma
Greater New Haven WPCA | New Haven | 345 EAST SHORE PARKWAY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/26/2021, 3:20 AM | 10/27/2021, 12:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined | flow meter/SCADA | 21.8 MGD | 21800000 | Yes | NEW HAVEN HARBOR
Greater New Haven WPCA | New Haven | 345 EAST SHORE PKWY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/27/2021, 12:00 AM | 10/27/2021, 12:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined | flow meter/SCADA | 0 | 0 | Yes | NEW HAVEN HARBOR
Greater New Haven WPCA | New Haven | 345 EAST SHORE PKWY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/30/2021, 5:27 AM | 10/30/2021, 7:15 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined | flow meter | 0.8 MG | 800000 | Yes | NEW HAVEN HARBOR
Greater New Haven WPCA | New Haven | 345 EAST SHORE PKWY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/4/2021, 10:11 PM | 10/5/2021, 12:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined |  | 2.4 mg | 2400000 | Yes | New Haven Harbor
Greater New Haven WPCA | New Haven | 345 EAST SHORE PKWY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/5/2021, 12:00 AM | 10/5/2021, 12:45 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined |  | 0.6 MGD | 600000 | Yes | NEW HAVEN HARBOR
Greater New Haven WPCA | New Haven | 345 EAST SHORE PARKWAY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 11/13/2021, 4:29 PM | 11/13/2021, 5:30 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined | Flow meter/totalizer | 0.4 MG | 400000 | Yes | New Haven Harbor | 64.2 min duration
Greater New Haven WPCA | New Haven | 345 EAST SHORE PARKWAY | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/16/2021, 11:46 AM | 10/17/2021, 12:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined | SCADA | 0.1 MGD | 100000 | Yes | New Haven Harbor
Greater New Haven WPCA | New Haven | 345 E Shore Pkwy, New Haven, CT | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 12/6/2021, 06:00 AM | 12/6/2021, 06:45 AM | Treatment Plant |  | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | SCADA | 0.4 MGD | Flow Meter/SCADA | 0.4 MG | 400000 | Yes | New Haven Harbor | Flows decreased
Greater New Haven WPCA | New Haven | 720 Foxon Rd, East Haven | Sewage Bypass | Dry | 1/17/2021, 8:05 PM | 1/17/2021, 8:30 PM | Manhole | Yes | Raw Sewage | Sewer Line Blockage - Grease | East Haven Police called it in. | 1-50 gallons | Field estimate by crew. | Less than 25 gallons. | 25 | No | N/A | Crew arrived at 720 Foxon and found water coming from the pick holes in the manhole cover. The crew jetted the line and restored flow. The line was blocked with grease. The area around the manhole cover was cleaned. The crew will return Tuesday to clean and CCTV inspect the line. Refer to work order #161957 for details.
Greater New Haven WPCA | New Haven | 47 Homelands Terr Hamden CT | Sewage Bypass | Dry | 1/20/2021, 11:05 AM | 1/20/2021, 12:20 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | Contractor called it in. | 51 - 500 gallons | Field estimate by crew. | Less than 100 gallons. | 100 | No | N/A | Contractor installed new utility pole over sanitary sewer. The sanitary sewer was broken causing some sewage to pass through the sanitary line, and some to seep out around the pole. The contractor removed the pole for the GNHWPCA contractor to repair the sanitary line.
Greater New Haven WPCA | New Haven | 121 Waite St Hamden CT | Sewage Bypass | Dry | 2/13/2021, 4:10 PM | 2/13/2021, 4:45 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner called it in. | 51 - 500 gallons | Field estimate by crew. | 377 gallons. .5'(.041')x30'x40'x7.48=376.99 gallons. | 377 | No | N/A | Crew arrived to find the sanitary sewer surcharged. The crew jetted the line and restored flow. The line was blocked with grease. The crew checked the home for damage. The basement floor was wet with puddling. It was noted there are two cleanouts in the floor, and both caps were off. There was a towel stuffed in one pipe, and the cap was sitting at the second. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 25 Morris Causway New Haven CT | Sewage Bypass | Dry | 2/16/2021, 9:15 PM | 2/16/2021, 9:50 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner called it in. | 1-50 gallons | Less than 15 gallons. | Field estimate by crew. | 15 | No | N/A | Crew arrived on site and found the line surcharged. The line was jetted and flow restored. The line was blocked with grease. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 243 Helen St Hamden St Hamden. | Sewage Bypass | Dry | 3/12/2021, 8:15 AM | 3/12/2021, 8:45 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Resident called it in. | 1-50 gallons | Field estimate by crew. | Less than 10 gallons. | 10 | No | N/A | Crew arrived at 243 Helen and found the line surcharged. The crew jetted the line and restored flow. The line was full of grease. The homeowner had sewage come up in a shower stall and toilet. There was a little overflow that spilled on the floor. Most of the sewage was contained in the shower stall. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 325 Franklin Rd Hamden | Sewage Bypass | Dry | 3/12/2021, 8:45 PM | 3/12/2021, 9:20 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner called it in. | 501 - 1,000 gallons | Field estimate by crew. | Basement was 25x35 with 1.5" totaling 818 gallons. | 818 | No | N/A | Crew arrived on location and found the sanitary sewer surcharged. The line was chased back to State St in front of the State St pump station. The line was jetted and flow restored. The line had heavy grease causing the blockage. The crew checked the property for damage. Pro Klean was contacted to clean and sanitize.
Greater New Haven WPCA | New Haven | 291 Franklin Rd Hamden | Sewage Bypass | Dry | 3/12/2021, 8:45 PM | 3/12/2021, 9:20 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner called it in. | 1-50 gallons | Field estimate by crew. | Less than 50 gallons. | 50 | No | N/A | Crew arrived on location and found the sanitary sewer surcharged. The line was chased back to State St in front of the State St pump station. The line was jetted and flow restored. The line had heavy grease causing the blockage. The crew checked the property for damage. Pro Klean was contacted to clean and sanitize.
Greater New Haven WPCA | New Haven | 2039 Dixwell Ave Hamden | Sewage Bypass | Dry | 3/15/2021, 12:25 PM | 3/15/2021, 12:50 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Crew found it when on PM sanitary sewer cleaning. | 1-50 gallons | Field estimate by crew. | Less than 10 gallons. | 10 | No | N/A | Crew found water starting to bubble out of the MHC when on PM sanitary sewer cleaning. The crew jetted the line and restored flow. The area around the cover was cleaned. Less than 10 gallons was discharged from the MH. The line was blocked with grease. The IPP dept. will be notified of the grease in the line.
Greater New Haven WPCA | New Haven | 1072 Dixwell Ave Hamden CT | Sewage Bypass | Dry | 3/20/2021, 2:15 PM | 3/20/2021, 3:15 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Property owner called it in. | 51 - 500 gallons | Field estimate by crew. | 63 gallons were discharged into the basement. | 63 | No | N/A | Crew spoke to the owner. Owner stated the problem was ongoing for 3 days. He stated he had a contractor snake his lateral. The crew jetted the line and pulled grease out. The line did not appear surcharged. After jetting the water stopped spilling into the basement.
Greater New Haven WPCA | New Haven | 16 Tuttle St New Haven CT | Sewage Bypass | Dry | 3/6/2021, 7:30 PM | 3/6/2021, 8:10 PM | Manhole | null | Raw Sewage | Unknown | Resident called it in. | 1-50 gallons | Field estimate by crew. | Less than 25 gallons. | 25 | No | N/A | Caller stated water was coming out around the MH cover. There is no sanitary sewer on the GIS mapping. This may be an old private sewer. The crew found the MH and cleared it. The MH was very shallow and the material was septic. The line was jetted. Nothing was observed other than thick black septic material in the line. The GNH will investigate this further. The crew cleaned up around the MH. Some of the water in the street had froze due to the cold.
Greater New Haven WPCA | New Haven | 241 Fairview Ave Hamden CT | Sewage Bypass | Rain <1" per hour | 4/11/2021, 10:15 PM | 4/11/2021, 10:55 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | Homeowner called it in. | 1-50 gallons | Field estimate by crew. | less than 50 gallons. | 50 | No | N/A | Crew arrived to find a pile of rags in the MH invert. The line was cleaned and flow restored. There was also grease in the line. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 980 Prospect St Hamden CT | Sewage Bypass | Dry | 4/4/2021, 12:35 PM | 4/4/2021, 12:55 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | Resident called it in. | 51 - 500 gallons | Field estimate by crew. | Less than 200 gallons. | 200 | No | N/A | Call came in from roto Rooter for the backup. The GNH crew arrived and found the sanitary sewer surcharged. The line was jetted and flow restored. The line was blocked by roots in the main. The property has a pump system in the basement. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 274 Augur St Hamden CT | Sewage Bypass | Dry | 4/5/2021, 8:10 PM | 4/5/2021, 8:45 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Resident called it in. | 1-50 gallons | Field estimate by crew. | Less than 20 gallons. | 20 | No | N/A | Crew arrived to find the sanitary sewer surharged. The line was blocked with grease in the manhole drop pipe. The line was cleared and flow restored. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | 32 Mill Pond Heights Rd, East Haven CT | Sewage Bypass | Dry | 5/11/2021, 2:45 PM | 5/11/2021, 3:15 PM | Manhole | Yes | Raw Sewage | Unknown | Landscaper called it in. | 1-50 gallons | Field estimate by crew. | Less than 20 gallons. | 20 | No | N/A | Landscaper called in a MH cover that water had leaked from in a grassy area off the edge of the road. The crew arrived and found the MHC wet and the ground around it damp. The crew jetted the line and restored flow. Most of the water reported was from the jetting process. The area around the MHC was cleaned with the vac truck. Lime was applied to the area around the MHC.
Greater New Haven WPCA | New Haven | 243 Helen St Hamden CT | Sewage Bypass | Dry | 5/11/2021, 9:30 AM | 5/11/2021, 10:00 AM | Basement | Unknown at this time | Raw Sewage | Unknown | Homeowner called it in. | 1-50 gallons | Field estimate by crew. | Less than 20 gallons. | 20 | No | N/A | The GNHWPCA filed this report within the two hour requirement. After the report was filed it was determined the customers lateral was blocked inside the home. The GNH had the lateral push cam inspected. Material was behind the house trap. The lateral is still blocked. Customer was calling a contractor to clear her line. This was not blocked in the city line.
Greater New Haven WPCA | New Haven | 771 Grand Ave, New Haven CT | Sewage Bypass | Rain <1" per hour | 5/30/2021, 12:15 AM | 5/30/2021, 12:40 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Contractor called it in. | 1,001 - 5,000 gallons | Based on contractor estimate. | 1118 gallons | 1118 | No | N/A | Contractor called in the backup at 771 Grand Ave, New Haven. The contractor had cabled the line several times before opening the MHC in the street. The GNHWPCA crew checked the city line and found it surcharged. The line was jetted and flow restored. The line was full of grease. The contractor stated there was 2" of water in a room 30'x30'. The room was not finished.
Greater New Haven WPCA | New Haven | 252-254 Goffe Ter New Haven CT | Sewage Bypass | Dry | 6/1/2021, 11:25 AM | 6/1/2021, 11:55 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | Plumbing contractor called it in. | 51 - 500 gallons | Field estimate by crew. | Less than 100 gallons was discharged into the basement. | 75 | No | N/A | Plumbing contractor was removing a house trap for the owner. Pipe Safe contractor could not snake through the trap. When removing the cap the basement started to flood. The contractor was able to re-install the cap. The crew checked the city line, was surcharged. The line was jetted and flow restored. There was tree roots and grease in the line. Pro Klean was contracted to clean and sanitize.
Greater New Haven WPCA | New Haven | east shore parkway | Sewage Bypass | Dry | 6/28/2021, 12:00 PM | 6/28/2021, 1:45 PM | Treatment Plant | null | None | Mechanical Equipment Failure | visual | 1,001 - 5,000 gallons | visual estimate | <5000 gal | 3000 | Yes | new haven harbor | line is plant effluent, prior to chlorination. broken pipe under ground. Contractor struck pipe during repair of pipe, causing release into waterway. Pipe repaired
Greater New Haven WPCA | New Haven | 53 Orange St New Haven Ct. | Sewage Bypass | Dry | 8/25/2021, 10:55 AM | 8/25/2021, 11:30 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Property Management company called it in. | 1-50 gallons | Field estimate by crew. | Less than 25 gallons. | 25 | No | N/A | The crew arrived at the location and found the line surcharged and full of grease. The line was jetted and flow restored. The GNH is CCTV inspecting the line. Pro Klean was contracted to clean and sanitize the basement.
Greater New Haven WPCA | New Haven | 57 Orange St New Haven CT | Sewage Bypass | Dry | 8/25/2021, 10:55 AM | 8/25/2021, 11:30 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Property management company called it in. | 1-50 gallons | Field estimate by crew. | Less than 50 gallons. | 50 | No | N/A | Crew arrived and found the sewer surcharged. the line was jetted and flow restored. The GNH is CCTV inspecting the line. The line was full of grease. Pro Klean was contracted to clean and sanitize the basement.
26506071

## GREENWICH
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Greenwich - Grass Island WPCF | Greenwich | 69 Mallard Drive | Sewage Bypass | Dry | 3/9/2021, 3:50 PM | 3/9/2021, 4:00 PM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | We are conducting sewer rehabilitation (CIPP lining) that requires temporary bypass, the contractor's temporary bypass pipe fitting came unconnected. | 51 - 500 gallons | Visual and based on size of pipe | Approximately 500 gallons | 500 | Yes | Brothers Brook | Contractor had tested bypass with clean water prior to activating with sewage. Unfortunately, one fitting connection came loose after sewage bypass was started up. Contractor was able to stop system almost immediately to limit the event.
Greenwich - Grass Island WPCF | Greenwich | 67 Harbor Drive | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:10 AM | 7/10/2021, 10:30 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By Sewer Division Field Staff performing routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Byram Harbor/Long Island Sound | Surcharging at Sewer Manhole 3761 due to heavy rains, excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 99 Glenwood Drive | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:10 AM | 7/9/2021, 7:47 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff performing routine inspections during storm event | Undetermined |  |  | 300 | Yes | Byram Harbor/Long Island Sound | Surcharging from two sanitary sewer manholes (Manhole numbers 3739 and 3738) on Glenwood Drive from excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 179 South Water Street | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:36 AM | 7/9/2021, 8:20 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff during routine inspection of system during storm event | Undetermined |  |  | 300 | Yes | Byram River | Surcharging manhole (MH # 1726) just south of MH 4716 previously reported - this is south of Hervey Street on South Water Street in Byram - due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 184 South Water Street | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:45 AM | 7/9/2021, 8:20 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event |  | Undetermined |  |  | 300 | Yes | Byram River | Surcharged sewer manhole (MH# 2495) on South Water Street north of Hervey Street due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 111 South Water Street to 77 South Water Street | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:45 AM | 7/9/2021, 8:20 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel performing routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Byram River | Four sewer manholes (MH #s 5140; 5139; 5138 and 5137) on South Water Street - wastewater trickling out around keyway due to excessive flows from Tropical Storm Elsa.
Greenwich - Grass Island WPCF | Greenwich | 184 and 163 South Water Street | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 8:52 AM | 7/9/2021, 8:20 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff doing routine system inspections during storm event | Undetermined |  |  | 300 | Yes | Byram River | Manhole Number 2496 on Hervey Street at South Water Street. Heavy Rain storm from Tropical Storm Elsa. Manhole surcharging small amount of diluted wastewater from the key hole of the manhole cover currently.
Greenwich - Grass Island WPCF | Greenwich | 169 South Water Street (for MH#s 2496 & 4716) and 88 South Water Street (for MH#s 5137 & 5138) | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 8:30 AM | 9/2/2021, 9:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system after the storm event | Undetermined |  |  | 150 | Yes | Byram River | Flow was just trickling around manhole covers
Greenwich - Grass Island WPCF | Greenwich | 250B Shore Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:15 AM | 7/10/2021, 2:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Coming out sewer manhole (no number) in parking lot of Grass Island Dog Park just upstream of Grass Island WWTP
Greenwich - Grass Island WPCF | Greenwich | 257 Shore Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:15 AM | 7/10/2021, 2:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Surcharging from sewer manhole (MH #1300) due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 251 Shore Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:15 AM | 7/10/2021, 2:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine system inspection during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Two sewer manholes surcharged and pouring out manhole covers - manhole numbers 5062 and 5063
Greenwich - Grass Island WPCF | Greenwich | 297 Shore Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:15 AM | 7/10/2021, 2:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff performing routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Surcharging sewer manhole (MH number 3712) due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | One Greenwich Plaza | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/9/2021, 8:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Surcharging manhole (MH #4399) due to excessive flows from Tropical Storm Elsa - this is just downstream from MH 4398 which was also still discharging at this time
Greenwich - Grass Island WPCF | Greenwich | One Greenwich Plaza | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/9/2021, 8:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Surcharging manhole (MH #4400) just downstream of 4401 - on Horseneck Lane - near Arch Street from excessive flows due to Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | One Greenwich Plaza | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:45 AM | 7/9/2021, 8:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel - performing routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Greenwich Harbor | Two Sewer Manholes (Manholes 4398 and 4401) on Arch Street and Horseneck Lane - surcharging out the keyhole of the manhole covers from heavy flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 1 Horseneck Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 10:30 AM | 9/2/2021, 3:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system after the storm event | Undetermined |  |  | 1000 | Yes | Greenwich Harbor | Sewer Manhole 4401 - on the corner of Horseneck Lane Train Station parking lot (at Horseneck and Arch Street)
Greenwich - Grass Island WPCF | Greenwich | 201-239 Shore Road (MHs 1292 and 4451) and 251-257 Shore Road (MHs 1436; 5063; 4449; 3701; 1300) | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 3:30 AM | 9/2/2021, 7:15 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system during the storm event | Undetermined |  |  | 1200 | Yes | Greenwich Harbor | Seven Sewer Manhole #s 1292; 4451; 1436; 5063; 4449; 3701; 1300 - observed around 3:30 a.m. - when crew rechecked between 7 a.m. and 7:15 a.m. the overflows had stopped
Greenwich - Grass Island WPCF | Greenwich | 1 Horseneck Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 5:30 AM | 9/2/2021, 7:15 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system during the storm event | Undetermined |  |  | 1000 | Yes | Greenwich Harbor | Sewer Manholes 4400 and 4401 - on the corner of the Horseneck Lane Train Station parking lot (at Horseneck and Arch Street) It had stopped by 7:15 a.m. when staff rechecked location
Greenwich - Grass Island WPCF | Greenwich | 1 Horseneck Lane | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 5:30 AM | 9/2/2021, 5:30 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system during the storm event | Undetermined |  |  | 1000 | Yes | Greenwich Harbor | Sewer Manholes 4400 and 4401 - on the corner of the Horseneck Lane Train Station parking lot (at Horseneck and Arch Street) It had stopped by 7:15 a.m. when staff rechecked location
Greenwich - Grass Island WPCF | Greenwich | 2 Steamboat Road/0 Arch Street | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 7:20 AM | 9/2/2021, 3:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | I personally saw it as a drove by manhole on way to Town Hall | Undetermined |  |  | 1000 | Yes | Greenwich Harbor | Sewage coming out around manhole cover
Greenwich - Grass Island WPCF | Greenwich | 250A Shore Road | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 7:50 AM | 9/2/2021, 8:15 PM | Treatment Plant | null | None | Excessive Flows - Storm Event | Visual inspection by Plant Maintenance Staff performing check of plant and equipment post storm event | Undetermined |  |  | 1000 | Yes | Greenwich Harbor | Partially treated sewage (post primary treatment) that had overflowed from the distribution chamber of the Aeration Tanks. Flow went into grass areas and a portion is going into the catch basin that eventually discharges to Greenwich Harbor
Greenwich - Grass Island WPCF | Greenwich | 84 Brookside Drive | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/10/2021, 9:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff during routine inspection of system during storm event | Undetermined |  |  | 300 | Yes | Horseneck Brook | Surcharging sewer manhole (MH #4482) on the Horseneck sewer line - due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 84 Brookside Drive | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/9/2021, 10:30 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff during routine inspection of system during storm event | Undetermined |  |  | 300 | Yes | Horseneck Brook | Surcharging sewer manhole (MH #4482) on the Horseneck sewer line - due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 84 Brookside Drive | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 12:00 AM | 9/4/2021, 12:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Field Manager went out to investigate and observed manhole overflowing | Undetermined |  |  | 1000 | Yes | Horseneck Brook | We do not have an exact start time for overflow, but based on the visual inspection today and based on the flow conditions elsewhere in the collection system, as well as historical experience, we believe this overflow started last night around midnight. As of 4 p.m. on Sept. 2, 2021 it was still flowing out of the manhole and into the Brook
Greenwich - Grass Island WPCF | Greenwich | 84 Brookside Drive | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 12:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Field Manager went out to investigate and observed manhole overflowing | Undetermined |  |  | 1000 | Yes | Horseneck Brook | We do not have an exact start time for overflow, but based on the visual inspection today and based on the flow conditions elsewhere in the collection system, as well as historical experience, we believe this overflow started last night around midnight. As of 4 p.m. on Sept. 2, 2021 it was still flowing out of the manhole and into the Brook
Greenwich - Grass Island WPCF | Greenwich | 25 Indian Harbor Drive | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:00 AM | 7/9/2021, 7:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspection of system during storm event | Undetermined |  |  | 300 | Yes | Indian Harbor | Surcharging sewer mahole (MH #1202) on Davis Avenue at the intersection of Indian Harbor Drive - due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 18 Roosevelt Avenue | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/10/2021, 7:15 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel - during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Long Island Sound | Surcharging sewer manhole (MH #2738) - Roosevelt Avenue at Irvine Street - due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 7 Shore Road - Old Greenwich | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:30 AM | 7/9/2021, 7:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Long Island Sound | Surcharging sewer mahole (MH #2387) manhole in front of Sewer Pump Station "A" and also from influent wetwell hatch at Station "A" PS on Shore Road due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 12 Ballwood Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 11:10 AM | 7/9/2021, 7:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Personnel during routine inspections during storm event | Undetermined |  |  | 300 | Yes | Long Island Sound | Surcharging manhole (MH #2362) on Ballwood Road at intersection with Holman Lane - just trickling out the manhole key hole. Due to excessive flows from Tropical Storm Elsa
Greenwich - Grass Island WPCF | Greenwich | 18 Roosevelt Avenue | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 8:05 AM | 9/2/2021, 9:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system after the storm event | Undetermined |  |  | 1000 | Yes | Long Island Sound | MH 2738 - Roosevelt & Irvine
Greenwich - Grass Island WPCF | Greenwich | 11 Tods Driftway | Sewage Bypass | Dry | 3/27/2021, 2:30 PM | 3/27/2021, 3:30 PM | Sewer Main | No | Raw Sewage | Unknown | Reported by Parks and Recreation Employee | 1-50 gallons | Based on est. bathroom flows, time and visual | Less than 50 gallons | 50 | No | N/A | Flow was only from the south concession bathrooms. Sewer requested P&R staff to close bathrooms while we cleared blockage to limit SSO. Only small area of sand received SSO and that sand was removed after stoppage was relieved.
Greenwich - Grass Island WPCF | Greenwich | 110 Shore Road | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 8:05 AM | 9/2/2021, 8:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | By field crew performing inspections of the collection system after the storm event | Undetermined |  |  | 1000 | Yes | Ultimately Long Island Sound | MH 2697 - this receives the discharge from FM from Ballwood PS
Greenwich - Grass Island WPCF | Greenwich | 110 Shore Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:35 AM | 7/9/2021, 7:15 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Sewer Division Field Staff during routine inspections of system during storm event | Undetermined |  |  | 300 | Yes | Ultimately to Long Island Sound | Surcharging sewer manhole (MH #2697) on Shore Road at Grant Avenue - this is the manhole that Ballwood PS force main discharges into
Greenwich - Grass Island WPCF | Greenwich | 212 Sound Beach Avenue | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 11:45 AM | 7/10/2021, 7:00 AM | Basement | null | Raw Sewage | Excessive Flows - Storm Event | Reported by business owner (Sweet Peas - 212 Sound Beach Avenue) | Undetermined |  |  | 50 | No |  | Property owner reported sewage backing up into basement. The sewer mains were full due to the excessive flows and flooding in Old Greenwich from Tropical Storm Elsa. We cannot confirm actual time that backup stopped as this is private property and we were not contacted when issue stopped.
Greenwich - Grass Island WPCF | Greenwich | 48 Glenville Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 12:53 PM | 7/9/2021, 10:00 PM | Basement | null | Raw Sewage | Excessive Flows - Storm Event | Reported by private property owner - issue in the house | Undetermined |  |  | 50 | No |  | Property owner reported backup in the house. Sewer Division personnel checked sewer mains in area and there was no overflows, but the system was flowing full due to the excessive flows from Tropical Storm Elsa. Private property owner did not notify us when backup stopped - so we cannot confirm end time accurately.
Greenwich - Grass Island WPCF | Greenwich | 2 Glenn Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:25 AM | 7/9/2021, 10:30 AM | Basement | Yes | Raw Sewage | Excessive Flows - Storm Event | Reported by Property Owner | Undetermined |  |  | 50 | No |  | Backing up in property owner's basement from slop sink in the basement. Once Fire Department closed the valve on basement sink drain the backup stopped
17050

## GROTON - CITY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Groton, City of | Groton | Three Acre RD groton ct. 06340 | Sewage Bypass | Dry | 1/18/2021, 5:00 PM | 1/18/2021, 5:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Home owner | 1-50 gallons | Estimated |  | 30 | No
GROTON, CITY OF | Groton | 1 Bishop Ln, Groton, CT | Sewage Bypass | Dry | 12/27/2021, 10:00 AM | 12/27/2021, 03:15 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Grease | Resident reported | 50-100 Gallon Total | Visual Estimate, clean up | 50-100 Gallons | 75 | No |  | Jetting line to clean blockage
Groton, City of | Groton | Bishop Lane City of Groton | Sewage Bypass | Dry | 3/15/2021, 11:00 AM | 3/15/2021, 11:30 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | home owner | 1-50 gallons | estimated |  | 30 | No
Groton, City of | Groton | Madison PL | Sewage Bypass | Dry | 5/3/2021, 10:00 AM | 5/3/2021, 3:00 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | checking manholes | 1,001 - 5,000 gallons | estimated |  | 3000 | Yes | Birch Plain Creek | Cleaned area up and put lime down
Groton, City of | Groton | Fairview Ave | Sewage Bypass | Dry | 6/6/2021, 8:00 PM | 6/6/2021, 8:30 PM | Pump Station | No | Raw Sewage | Electrical Equipment Failure | Call-in for power outage | 51 - 500 gallons | approximate |  | 300 | No |  | Bad car accident took down multiple polls big power surge generator transfer switch didn't transfer. Shut of generator reset transfer switch generator come on and transferred over and pumps pumped down the wet well.
3435

## GROTON - TOWN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Groton, Town of | Groton | 118 Fort Hill Road | Sewage Bypass | Snowmelt | 2/12/2021, 10:05 AM | 2/12/2021, 11:00 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Resident | Undetermined | See Comments |  | 20 - Did not count as reaching water | Yes | Unknown if it was enough to reach Poquonnock river. See comments | Bypass reported to Town Hall by resident. Bypass was from manhole in small commerical parking lot. No visible flow , only trace evidence near manhole. Liquid level in manhole 2 feet below rim indicating partial line blockage. sewer line jetted to break blockage. Adjacent pavement clean with hypochlorite and water. No evidence showing bypass reached nearby catch basin. If it did, the catch basin drains via 3300 foot storm drain system to Poqk River. No evidence of bypass at outfall.
Groton, Town of | Groton | 1250 Poquonnock Road | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 4:30 AM | 9/2/2021, 5:30 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | WPCD staff noticed it | Undetermined |  |  | 100 | Yes | Poquonnock River | Sewage appeared to be seeping from a manhole in a roadway gutter area during extreme storm event. Manhole lid was not displaced. Runoff drained to nearby Poquonnock river. Sewage characteristic was clear grey water, no solids, very dilute from overnight storm event. Additional comment with 5 day report: IDK why the start time posted what it did. The start time

## HERITAGE VILLAGE
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Heritage Village | Southbury | 316 Heritage Rd | Sewage Bypass | null | 1/22/2021, 8:40 AM | 1/22/2021, 8:47 AM | Treatment Plant | No | Sludge Spill | Mechanical Equipment Failure | Operator | 51 - 500 gallons | The room is 10 ft. by 20 ft. Depth was 1 ft. Volume of sludge is 1500 gal. Approximately 100 gallons leaked under the door. | Approximately 100 gallons. | 100 | Yes | Pomperaug River | We used a sump pump with an 2 inch discharge hose to pump out the room into the aeration tank nearby.
Heritage Village | Southbury | 1200 South Britain Road, 2-A Traditions Blvd. | Sewage Bypass | Dry | 6/4/2021, 9:00 AM | 6/4/2021, 6:00 PM | Pump Station | null | Raw Sewage | Unknown | Operator found a sink hole next to wet well upon daily lift station inspection. Line was a force main from Southbury Training School | 1,001 - 5,000 gallons | Estimated | Less than 3000 | 2700 | Yes | Transylvania Brook | Force Main is from Southbury Training School. At this time it is unknown what body of water it flows into. The flow was going into a storm drain. The break was not from the force main for Southbury Training School. It was caused by a failure of the rubber seal in the coupling between the pump discharge and the check valve in the valve chamber. The two pipes are next to each other.

## JEWETT CITY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Jewett City WPCA | Griswold | 95 Pleasant View | Sewage Bypass | Dry | 8/24/2021, 8:30 AM | 8/24/2021, 8:30 AM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Roots | Operator observed manhole overflowing | 51 - 500 gallons | Visual |  | No |  | Trying to jet blockage and pumping out the manhole
Jewett City WPCA | Griswold | 52 Wedgewood Drive | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 5:00 AM | 9/2/2021, 7:00 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | SCADA | 5,001 - 20,000 gallons | Average flow to plant at time | 9,000 gallons | Yes | Quinnibaug | Flow exceeded 700gpm and went to flood storage tank and the tank overflowed

## LEBANON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Lebanon | Lebanon | 116 Deepwood Drive | Sewage Bypass | Dry | 9/16/2021, 3:00 PM | 9/16/2021, 4:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Call in of liquid on street | 1-50 gallons | No ponding or pooling in downhill direction, slow leak, and quick rectification |  | No

## LITCHFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Litchfield WPCF | Litchfield | 29 Stoddard Rd. | Sewage Bypass | Dry | 3/13/2021, 2:31 AM | 3/13/2021, 4:10 AM | Treatment Plant | null | None | Electrical Equipment Failure | Plant Superintendent responding to a power loss alarm at the treatment plant at 2:31 AM, | 0 | Aeration was only off for 45 minutes. | 0 | No | Terrence Donoghue | Plant loss line power at 2:31 AM. When plant Superintendent arrived at 3:07 AM. the plant generator was running but the plant transfer switch had not engaged properly, and plant had no power for about 45 minutes. Superintendent manually switched it and plant went back to line power and normal operations resumed. We will place a service call for the transfer switch and determine why it did not switch over as required.

## MANCHESTER
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Manchester | Danbury | 120 Thraw Road | Sewage Bypass | Dry | 10/22/2021, 10:00 AM | 10/19/2021, 10:10 AM | Treatment Plant | null | Sludge Spill | Mechanical Equipment Failure | Operator | 501 - 1,000 gallons | estimate | 500 gallons | 500 | Yes | Hockanum River | Operator was not paying attention and the centrifuge went to water and overflowed the sludge can.
Manchester | Manchester | 100 Union Street Manchester CT | Sewage Bypass | Dry | 3/6/2021, 2:00 PM | 3/6/2021, 2:00 PM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | DOT bridge inspection | 1-50 gallons | estimate |  | 30 | Yes | Hockanum River | This sewer main is located under a bridge. The DOT found it while inspecting the bridge. The pipe has got a drip. Kyle is in the process of getting someone to fix it.
Manchester | Manchester | 216 Weatherell Street | Sewage Bypass | Dry | 6/25/2021, 10:30 PM | 6/26/2021, 12:53 AM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Grease | Property owner abutting our Sewer easement found bypass while riding ATV in the woods. | 1,001 - 5,000 gallons | Visual Estimate |  | 3000 | Yes | Folly Brook
Manchester | Manchester | 194 Buckland Hill Drive | Sewage Bypass | Dry | 8/5/2021, 9:30 PM | 8/5/2021, 10:15 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Called in by mall manager | 51 - 500 gallons | Visual estimate |  | 300 | No
Manchester | Manchester | 120 Thrall Road | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 1:40 PM | 9/2/2021, 1:41 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | By a Operator sampling and monitoring | Over 1,000,000 gallons | To much flow to be determined |  | 1000000 | Yes | Hockanum River | Treatment plant had excessive flows due to storm Ida that over-whelemed the plant. All tanks and pumps were online. Solids were blown out of the plant with the high flow volume. All UV bulbs were online.
Manchester | Manchester | 120 Thrall Road | Sewage Bypass | Dry | 9/3/2021, 1:34 PM | 9/3/2021, 3:36 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Was discovered by the operator running the plant recording data related to UV | Over 1,000,000 gallons | Estimated |  | 1000000 | Yes | Hockanum River | While testing generator issues, the communication with the UV system was faulted. The UV system was not communicating proper info to the plant SCADA system and the data was appearing to be "Frozen". We notified and had Aaron Associates looking into the issue throughout the day. The "frozen" info was reading a much higher flow through the UV system and also reading a much lower dose than what was being acheived. During this time while the info was frozen, ALL UV bulbs were ON. Problem is fixed.
2003830

## MATTABASSET
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Mattabassett District | Cromwell | 245 Main St, Cromwell CT 06416 | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 11:08 AM | 7/9/2021, 11:08 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Visual | Undetermined |  |  | 34580000 | Yes | CT river
Mattabassett District | Cromwell | 245 Main St. Cromwell CT 06416 | Sewage Bypass | Rain <1" per hour | 9/2/2021, 1:20 AM | 9/2/2021, 1:20 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | Operator opened gate | Undetermined |  |  | 41150000 | Yes | Connecticut River
Mattabassett District | Cromwell | 244 Deming Road, Berlin, CT | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 11:04 PM | 9/2/2021, 1:05 PM | Sewer Main | No | Raw Sewage | Excessive Flows - Storm Event | Mattabassett District employee inspecting manholes along sewer trunkline | 50,001 - 100,000 gallons | Estimate |  | 75000 | No |  | Mattabassett employee inspected manholes after historic storm event and found evidence of surcharging manhole into the backyard of 244 Deming Road Berlin CT. Insurance company was called and clean up is being coordinated with property owner.
75805000
75730000

## MDC
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
The Metropolitan District | Bloomfield | 67 Ledyard Ave | Sewage Bypass | Dry | 3/25/2021, 11:16 AM | 3/25/2021, 12:00 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other |  | 1-50 gallons | MDC PERSONELL | LESS THEN 1 GALLON | 1 | No |  | Home owner originally stated to MDC that there was no spill. Information provided further into investigation showed a spill of less than 1 gallon - EVENT HAS ENDED
The Metropolitan District | Bloomfield | 500 COTTAGE GROVE RD | Sewage Bypass | Dry | 3/30/2021, 2:32 PM | 3/30/2021, 2:32 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Roots | MDC PERSONELL | 1-50 gallons | MDC PERSONELL | <50 gal | 30 | No |  | DISCHARGE WAS IN RIGHT OF WAY - DISCHARED TO SOIL - NO HOUSES AFFECTED - EVENT HAS ENDED
MDC COLLECTIONS | East Hartford | 22 Woodlawn Cir, East Hartford, CT | Sewage Bypass | Dry | 12/24/2021, 06:45 PM | 12/24/2021, 08:45 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Grease | PASSERBY | 1000 - 2500GALS | MDC PERSONNEL | <1000 GALS | 950 | Yes | HOCKANUM RIVER | Jet truck cleared blockage
The Metropolitan District | East Hartford | 40 Willow Brook rd East Hartford | Sewage Bypass | Dry | 3/1/2021, 6:25 PM | 3/1/2021, 7:30 PM | null | null | Raw Sewage | Sewer Line Blockage - Other |  | Undetermined |  |  | 100 | No
The Metropolitan District | East Hartford | MAIN ST | Sewage Bypass | Dry | 3/4/2021, 10:23 PM | 3/4/2021, 11:27 PM | Basement | Yes | Raw Sewage | Unknown | HOMEOWNER | Undetermined | MDC CLAIMS AGENT | Less than 10g | 5 | No |  | Less than 10g bypass - Event has ended
The Metropolitan District | East Hartford | 10-12 Beaumont st | Sewage Bypass | Dry | 4/25/2021, 12:15 AM | 4/24/2021, 1:30 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner | Undetermined |  |  | 10 | No
The Metropolitan District | East Hartford | 343 HIGH ST | Sewage Bypass | null | 9/2/2021, 4:05 PM | 9/2/2021, 10:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | 1,001 - 5,000 gallons |  |  | 3000 | No |  | OVERFLOW DUE TO WET WEATHER EVENT - EVENT HAS ENDED
4065
MDC COLLECTIONS | Hartford | Capitol Ave and Park Ter, Hartford, CT | Sewage Bypass | Dry | 12/19/2021, 08:45 PM | 12/19/2021, 10:30 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Other | MDC SCADA | <10000g | MDC SCADA | 0.349mg | 349000 | Yes | Park River | Main sewer jetted and relieved by MDC forces
MDC COLLECTIONS | Hartford | Arlington St, Hartford, CT | Sewage Bypass | Dry | 12/24/2021, 09:30 PM | 12/25/2021, 03:30 AM | Sewer Main |  | Raw Sewage | Other | HARTFORD FIRE DEPT | TO BE DETERMINED | MDC SCADA | 0.069mg | 69000 | Yes | SOUTH BRANCH PARK RIVER | Repaired Water Main break
The Metropolitan District | Hartford | Capitol Ave at Park View Terr | Sewage Bypass | Dry | 10/28/2021, 5:35 PM | 10/28/2021, 6:15 PM | Sewer Main | null | Raw Sewage | Unknown | SCADA | 51 - 500 gallons | SCADA | 14000 | 14000 | Yes | Park River Conduit | BYPASS PUMING ISSUES secondary clearifier takin offline due to oil leakage
The Metropolitan District | Hartford | 32 SANFORD ST | Sewage Bypass | Dry | 10/3/2021, 11:40 AM | 10/3/2021, 1:45 PM | Sewer Main | null | Raw Sewage | Unknown | SCADA | 51 - 500 gallons | MDC Personnel | 1000 Gallons | 1000 | Yes | CONNECTICUT RIVER
The Metropolitan District | Hartford | 13 FAIRMONT ST HARTFORD | Sewage Bypass | Dry | 3/30/2021, 4:30 PM | 3/30/2021, 11:00 PM | Basement | Yes | Raw Sewage | Unknown | MDC PERSONNEL | 1-50 gallons | MDC PERSONNEL | LESS THAN 1g | 950 | No |  | BYPASS WAS LESS THAN 1g REPAIRS COMPLETED. EVENT HAS ENDED
The Metropolitan District | Hartford | MONTROSE ST. @ NEW BRITAIN AVE | Sewage Bypass | Dry | 6/16/2021, 6:02 AM | 6/16/2021, 6:53 AM | Manhole | No | Raw Sewage | Mechanical Equipment Failure | MDC SCADA SYSTEM | 5,001 - 20,000 gallons | MDC SCADA SYSTEM | 11,000gal | 11000 | Yes | PARK RIVER | OVERFLOW DUE TO WATER MAIN BREAK AT 47 MONTROSE ST - WATER MAIN SHUT DOWN - OVERFLOW HAS ENDED
The Metropolitan District | Hartford | 23 Green Manor Ave | Sewage Bypass | Dry | 7/15/2021, 4:00 PM | 7/15/2021, 4:30 PM | Basement | Unknown at this time | Raw Sewage | Unknown | Homeowner | Undetermined | MDC CLAIMS AGENT | LESS THAN 1000g | 950 | No |  | bypass due to debris in m/s - event has ended
The Metropolitan District | Hartford | SANFORD ST @ BELLEVUE ST | Sewage Bypass | Dry | 9/3/2021, 2:15 PM | 9/3/2021, 3:45 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 22000 gal | 22000 | Yes | CT RIVER | POSSIBLE DEBRIS FROM WET WEATHER EVENT CAUSING OVERFLOW
The Metropolitan District – Hartford WPCF | Hartford | 240 Brainard Road | Sewage Bypass | Rain <1" per hour | 4/21/2021, 5:33 PM | 4/21/2021, 5:38 PM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | SCADA alarm system made notification of high wet well level for response by operator. | 1,001 - 5,000 gallons | Visual observation | N/A | 1000 | No |  | The incident was the result of a failed new "fast acting gate" that was installed during the facilities recent upgrade. The gate was signaled to close due to our CEPS pumps cycling to accommodate increasing flows from rain. The cycle of the CEPS pumps caused a ripple in the outfall that tripped a high float at UV, signaling the "fast acting gate" to close. The issue resulted from the "fast acting gate" not opening back up backing up flows into the secondary creating a momentary overflow.
[15 empty] | 468900 |  | 443000
The Metropolitan District | Newington | Brookside Rd - Newington | Approved Bypass for Constrution Projects | Dry | 1/7/2021, 9:15 AM | 1/8/2021, 11:30 AM | Pump Station | null | Raw Sewage | Approved Bypass for Construction |  | Undetermined | MDC PERSONNEL | 0 gallons | 0 | No |  | Planned bypass at Sewer Pump Station for scheduled maintenance. Bypass will only during day time hours, but will be over several days. 357,000g went through the bypass. BYPASS HAS NOW ENDED
The Metropolitan District | Newington | Prince St | Sewage Bypass | Dry | 2/17/2021, 11:00 AM | 2/17/2021, 9:20 AM | Basement | Yes | Raw Sewage | Unknown | MDC CLAIMS AGENT | Undetermined | MDC CLAIMS AGENT | <100g | 50 | No |  | MAIN LINE BLOCKAGE - EVENT HAS ENDED - HOME OWNER REPORTED INCIDENT AFTER THE EVENT WAS OVER
The Metropolitan District | Newington | 37 PRINCE AVE | Sewage Bypass | Dry | 2/17/2021, 9:15 AM | 2/17/2021, 9:20 AM | Basement | Unknown at this time | Raw Sewage | Unknown | HOME OWNER | Undetermined | MDC CLAIMS AGENT | <100g | 50 | No |  | MAIN LINE BLOCKAGE IN SEWER - RELIEVED - EVENT HAS ENDED
The Metropolitan District | Newington | 45 PRINCE AVE | Sewage Bypass | Dry | 2/17/2021, 9:15 AM | 2/17/2021, 9:20 AM | Basement | Yes | Raw Sewage | Unknown | HOME OWNER | Undetermined | MDC CLAIMS AGENT | <100g | 50 | No |  | MAIN LINE BLOCKAGE - RELIEVED - EVENT HAS ENDED
The Metropolitan District | Newington | 41 PRINCE AVE | Sewage Bypass | Dry | 2/17/2021, 9:15 AM | 2/17/2021, 9:20 AM | Basement | Yes | Raw Sewage | Unknown | HOME OWNER | Undetermined | MDC CLAIMS AGENT | <100g | 50 | No |  | MAIN LINE BLOCKAGE - relieved - event has ended
The Metropolitan District | Newington | 111 CARR AVE - NEWINGTON | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:55 AM | 7/9/2021, 8:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined | MDC PERSONNEL | 200,000g | 200000 | Yes | WEBSTER BROOK | BYPASS DUE TO WET WEATHER EVENT
The Metropolitan District | Newington | 98 CARR AVE NEWINGTON | Sewage Bypass | null | 9/2/2021, 12:54 AM | 9/2/2021, 3:45 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | EMERG PLANNED BYPASS | 1,001 - 5,000 gallons | MDC PERSONNEL | 385,860g | 385860 | Yes | WEBSTER BROOK | BYPASS DUE TO RAIN EVENT - EVENT HAS ENDED
586060
The Metropolitan District | Rocky Hill | 58 Glastonbury Ave - Rocky Hill | Sewage Bypass | Rain <1" per hour | 3/1/2021, 9:38 AM | 3/1/2021, 4:15 PM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | MDC PERSONNEL | 1-50 gallons | MDC PERSONNEL | 100g - 1000g | 150 | Yes | CT RIVER | Possible Break in sewer force main. MDC Repair crews in route. EVENT HAS ENDED - ALL REPAIRS COMPLETED
The Metropolitan District | West Hartford | Hillcrest Ave | Sewage Bypass | Rain <1" per hour | 1/16/2021, 7:54 AM | 1/16/2021, 6:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 1.318mg | 1318000 | Yes | Piper Brook | WET WEATHER EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | Hillcrest Ave - West Hartford | Sewage Bypass | Rain <1" per hour | 10/26/2021, 1:37 PM | 10/26/2021, 11:24 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | 501 - 1,000 gallons | MDC SCADA SYSTEM | 868,000G | 868000 | Yes | Piper Brook | NTS - Hillcrest - Overflow due to Wet Weather Event- EVENT HAS ENDED
The Metropolitan District | West Hartford | 17 Mozart St West Hartford | Sewage Bypass | Rain <1" per hour | 10/26/2021, 11:13 PM | 10/27/2021, 12:15 AM | Basement | Yes | Raw Sewage | Unknown | HOMEOWNER | 1-50 gallons | MDC PERSONAL |  | 50 | No |  | Main sewer jetted stoppage relieved
The Metropolitan District | West Hartford | TROUT BROOK DR | Sewage Bypass | Dry | 2/25/2021, 5:30 PM | 2/25/2021, 6:35 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | HOMEOWNER | Undetermined | MDC CLAIMS AGENT | <100g | 75 | No |  | EVENT HAS ENDED
The Metropolitan District | West Hartford | HILLCREST AVE - WEST HARTFORD | Sewage Bypass | Rain <1" per hour | 3/1/2021, 10:18 AM | 3/1/2021, 11:39 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 38000g | 38000 | Yes | PIPER BROOK | OVERFLOW EVENT DUE TO WET WEATHER & SNOW MELT
The Metropolitan District | West Hartford | HILLCREST DR | Sewage Bypass | Rain <1" per hour | 4/15/2021, 11:08 PM | 4/16/2021, 4:32 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 0.063mg | 63000 | Yes | PIPER BROOK | NTS - HILLCREST - BYPASS DUE TO WET WEATHER - EVENT HAS ENDED
The Metropolitan District | West Hartford | HILLCREST AVE | Sewage Bypass | Rain <1" per hour | 5/30/2021, 11:34 PM | 5/31/2021, 2:06 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 0.003MG | 3000 | Yes | PIPER BROOK | RAIN EVENT HAS ENDED
The Metropolitan District | West Hartford | OPP #204 TROUT BROOK WH | Sewage Bypass | Rain <1" per hour | 7/18/2021, 3:36 AM | 7/18/2021, 3:56 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event |  | Undetermined |  |  | 3000 | Yes | TROUT BROOK
The Metropolitan District | West Hartford | 24 Deepwood Lane West Hartford | Sewage Bypass | Dry | 7/25/2021, 5:40 PM | 7/25/2021, 7:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | West Hartford PD | Undetermined | MDC personnel visual observation |  | 150 | Yes | town of west hartford storm drainage | Disregard 1st report, filed prematurely.
The Metropolitan District | West Hartford | Hillcrest Ave - West Hartford | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 8:20 AM | 7/11/2021, 5:45 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 17.174mg | 17174000 | Yes | Piper Brook | OVERFLOW DUE TO RAIN EVENT EVENT IS ONGOING
The Metropolitan District | West Hartford | Talcott Rd @ Chelton Ave | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 8:36 AM | 7/10/2021, 3:52 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 7.373mg | 7373000 | Yes | Troutbrook | OVERFLOW DUE TO WET WEATHER EVENT EVENT IS ONGOING - FINAL REPORT TO FOLLOW
The Metropolitan District | West Hartford | Troutbrook Ave N/O Quaker Ln - West Hartford | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 8:46 AM | 7/10/2021, 2:49 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 392,000g | 392000 | Yes | TROUTBROOK | OVERFLOW DUE TO RAIN EVENT EVENT HAS ENDED -
The Metropolitan District | West Hartford | REAR #1 FOX MEADOW LN - WH | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:45 AM | 7/10/2021, 2:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined | MDC PERSONNEL |  | 300000 | Yes | TROUTBROOK | SURCHARGED DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | FOX MEADOW LN - WH | Sewage Bypass | Rain 2-3" per hour | 8/19/2021, 3:15 PM | 8/19/2021, 5:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONELL | Undetermined | MDC PERSONELL | 2.06m | 2060000 | Yes | TROUTBROOK | OVERFLOW DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | CTS - 2 - TROUTBROOK LN @ QUAKER LN | Sewage Bypass | Rain 1-2" per hour | 8/19/2021, 7:52 AM | 8/19/2021, 11:15 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 1.679m | 1679000 | Yes | TROUTBROOK | OVERFLOW DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | CHELTON AVE | Sewage Bypass | Rain 1-2" per hour | 8/19/2021, 8:58 AM | 8/19/2021, 1:19 PM | null | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | 20,001 - 50,000 gallons | MDC SCADA SYSTEM | 1.779m | 1779000 | Yes | TROUTBROOK | OVERFLOW DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | HILLCREST AVE - WH | Sewage Bypass | Rain 1-2" per hour | 8/19/2021, 9:52 AM | 8/19/2021, 2:22 PM | null | No | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | Undetermined | MDC SCADA SYSTEM | 2.06m | 2060000 | Yes | PIPER BROOK - WH | NTS - OVERFLOW DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | 115 HILLCREST AVE | Sewage Bypass | Rain 1-2" per hour | 8/22/2021, 2:24 PM | 8/22/2021, 2:34 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | SCADA | 100,001 - 500,000 gallons | SCADA | 3.90 MG | 3900000 | Yes | PIPER BROOK
The Metropolitan District | West Hartford | 35 RINGGOLD ST | Sewage Bypass | Rain 1-2" per hour | 8/22/2021, 2:30 PM | 8/24/2021, 11:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined | MDC PERSONNEL | 25,OOOg | 25000 | Yes | TROUT BROOK | overflow was not constant through this rain event - EVENT HAS ENDED
The Metropolitan District | West Hartford | Talcott Rd at Chelton Ave | Sewage Bypass | Rain 1-2" per hour | 8/22/2021, 2:42 PM | 8/22/2021, 11:30 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | SCADA | 100,001 - 500,000 gallons | SCADA | SCADA | 30000 | Yes | Trout Brook
The Metropolitan District | West Hartford | 204 Trout Brook Dr. | Sewage Bypass | Rain 1-2" per hour | 8/22/2021, 3:06 PM | 8/22/2021, 5:30 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | SCADA | 100,001 - 500,000 gallons | SCADA | 40,000 GALLONS | 40000 | Yes | Trout Brook
The Metropolitan District | West Hartford | 204 Trout Brook Dr. | Sewage Bypass | Rain 1-2" per hour | 8/23/2021, 1:05 PM | 8/23/2021, 8:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | SCADA | 100,001 - 500,000 gallons | SCADA | 154000 Gallons | 154000 | Yes | Trout Brook | CTS - 2
The Metropolitan District | West Hartford | 115 Hillcrest Ave | Sewage Bypass | Rain 1-2" per hour | 8/23/2021, 12:44 PM | 8/24/2021, 10:34 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | 100,001 - 500,000 gallons | MDC SCADA SYSTEM | 9.205mg | 9205000 | Yes | Piper Brook | NTS - overflow due to wet weather event - EVENT HAS ENDED
The Metropolitan District | West Hartford | Talcott Rd at Chelton Ave. | Sewage Bypass | Rain 1-2" per hour | 8/23/2021, 12:48 PM | 8/24/2021, 11:54 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA SYSTEM | 100,001 - 500,000 gallons | MDC SCADA SYSTEM | 6.311mg | 6311000 | Yes | Trout Brook | CTS-3 OVERFLOW DUE TO WET WEATHER EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | 115 Hillcrest Ave | Sewage Bypass | Rain 1-2" per hour | 9/1/2021, 5:36 PM | 9/4/2021, 9:15 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA | 100,001 - 500,000 gallons | MDC SCADA | 20.525m | 20525000 | Yes | Piper Brook | NTS - overflow due to wet weather event - EVENT HAS ENDED
The Metropolitan District | West Hartford | Talcott Rd @ Chelton Ave | Sewage Bypass | Rain 1-2" per hour | 9/1/2021, 8:20 PM | 9/3/2021, 3:00 AM | null | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA | Undetermined | MDC SCADA | 9.33m | 9330000 | Yes |  | Overflow due to wet weather event - EVENT HAS ENDED
The Metropolitan District | West Hartford | 204 Talcott Rd West Hartford | Sewage Bypass | Rain 1-2" per hour | 9/1/2021, 9:11 PM | 9/2/2021, 4:40 PM | null | null | Raw Sewage | Excessive Flows - Storm Event | MDC SCADA | Undetermined | MDC SCADA | 3.151m | 3151000 | Yes | TROUT BROOK | Overflow due to wet weather event - EVENT HAS ENDED
The Metropolitan District | West Hartford | 35 RINGGOLD ST | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 10:00 AM | 9/3/2021, 11:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined | MDC PERSONNEL | 1000 - 25000 | 10000 | Yes | TROUT BROOK | SURCHARGE DUE TO HEAVY RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | Brightview Dr. at North Main St. | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 11:18 AM | 9/3/2021, 11:30 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | MDC Personal | 20,001 - 50,000 gallons |  |  | 30000 | No |  | OVERFLOW DUE TO RAIN EVENT - EVENT HAS ENDED
The Metropolitan District | West Hartford | S QUAKER LN @ TROUTBROOK DR | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 3:00 PM | 9/3/2021, 12:30 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | TOWN OF WEST HARTFORD REPORTED TO MDC | 501 - 1,000 gallons |  |  | 1000 | Yes | TROUTBROOK | OVERFLOW DUE TO RAIN EVENT - event has ended
The Metropolitan District | West Hartford | 1 FOX MEADOW LN - WH (REAR) | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 5:30 AM | 9/3/2021, 12:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined |  |  | 1000 | Yes | Troutbrook | SURCHARGED DUE TO RAIN EVENT
The Metropolitan District | West Hartford | RAYMOND RD | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 8:30 AM | 9/2/2021, 11:00 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | 501 - 1,000 gallons | MDC PERSONNEL |  | 1000 | Yes | TROUT BROOK | REPORTED BY TOWN OF WEST HTFD - OVERFLOW HAD STOPPED AT TIME OF MDC VISIT - EVENT HAS ENDED
[15 empty] | 87824275 |  | 55896000 | 23310000
The Metropolitan District | Wethersfield | OLNEY RD | Sewage Bypass | Dry | 4/2/2021, 5:39 PM | 4/2/2021, 6:00 PM | Basement | null | Raw Sewage | Unknown | Plumber / Contractor | 1-50 gallons |  |  | 50 | No
The Metropolitan District | Wethersfield | WELLS RD @ SPRING ST - WETHERSFIELD | Sewage Bypass | Rain <1" per hour | 9/3/2021, 10:30 AM | 9/3/2021, 4:10 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | MDC PERSONNEL | Undetermined |  |  | 1000 | Yes | WET LANDS | OVERFLOW WAS DISCOVERED LATE IN THE EVENT - OVERFLOW HAS ENDED
The Metropolitan District | Windsor | 6 LONDON RD - WINDSOR | Sewage Bypass | Dry | 7/17/2021, 2:40 PM | 7/15/2021, 4:30 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | REPORTED BY HOMEOWNER | Undetermined | MDC PERSONNEL | LESS THAN 1000g | 1000 | No |  | BYPASS LESS THAN 1000g - EVENT HAS ENDED
The Metropolitan District – Poquonock WWTF | Windsor | 1222 Poquonock Ave Windsor Ct 06095 | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 5:25 AM | 9/2/2021, 11:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Monitoring equipment | Undetermined | Weir elevation | 378000 | 378000 | Yes | Farmington River

## MERIDEN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Meriden | Meriden | 20 windsor ave | Sewage Bypass | Dry | 1/10/2021, 9:47 PM | 1/10/2021, 11:10 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | passer by | 1-50 gallons | visual |  | 25 | No |  | small amount of sewage reached a catch basin. Area was cleaned up and light HTH application
Meriden | Meriden | Myrtle St. and Arch Parkway intersection | Sewage Bypass | Dry | 1/6/2021, 12:25 PM | 1/6/2021, 1:31 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | passer by | 1-50 gallons | visual |  | 25 | No |  | sewage reach a catch basin. after blockage was released clean up and light HTH application
Meriden | Meriden | 785 east main street | Sewage Bypass | Dry | 5/15/2021, 5:00 PM | 5/15/2021, 8:30 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | passer by | 1-50 gallons | visual |  | 25 | No |  | wendy's restaurant on east main street in meriden, grease vault is full and leaking out of manhole covers. we shut down the restaurant until they have this problem taken care of. meriden health department is aware and is following up with an inspection prior to them reopening. leaked into a catch basin in middle of driveway. restaurant had grease tank pumped out and sewer line cleaned and catch basin pumped out.
Meriden | Meriden | 1672 north colony | Sewage Bypass | Dry | 5/18/2021, 12:30 PM | 5/18/2021, 2:05 PM | Lateral - Private | Yes | Raw Sewage | Sewer Line Blockage - Other | passer by | 1-50 gallons | visual |  | 25 | No |  | partial blockage of city sanitary main caused by rags, ppe, grease caused the private force main to discharge through a clean out on the force main. relieved partial blockage and clean up area , applying light hth
Meriden | Meriden | 226 Evansville Ave | Sewage Bypass | Rain > 4" per hour | 7/9/2021, 11:20 AM | 7/9/2021, 5:15 PM | Pump Station | No | Raw Sewage | Excessive Flows - Storm Event | Scada Alarm, and Staff monitoring | 500,001 - 999,999 gallons | Flow meter | 1.37 mg | 1370000 | Yes | Quinnipiac River | flow is mostly rain water
Meriden | Meriden | between 9 and 21 Rose Circle | Sewage Bypass | Rain 1-2" per hour | 8/23/2021, 10:00 AM | 8/23/2021, 11:15 AM | Manhole | No | Raw Sewage | Mechanical Equipment Failure | By staff driving by | 501 - 1,000 gallons | visual estimation |  | 700 | Yes | Meetinghouse Brook | Air relief valve leaking on 20" force main filling up manhole. We are currently bypass pumping from manhole into close by gravity sewer to keep everything contained.
Meriden | Meriden | 226 evansville ave meriden ct | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 1:35 AM | 9/2/2021, 9:45 AM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | scada notification | Undetermined | flow meter | 2.01 million gallons | 2010000 | Yes | Quinnipiac river
[15 empty] | 3380800 |  | 3380000

## MIDDLETOWN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Middletown WPCF | Middletown | 42 Columbus ave Middletown Ct | Sewage Bypass | Dry | 1/30/2021, 11:54 AM | 1/30/2021, 12:56 PM | Sewer Main | Yes | None | Sewer Line Blockage - Other | Home owner at 42 Columbus | 0 | contained to basement | 0 | 0 | No |  | Found Cloth rag in main causing blockage
Middletown WPCF | Middletown | Pameecha ave | Sewage Bypass | Rain <1" per hour | 10/4/2021, 10:00 AM | 10/4/2021, 12:00 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | Staff | Undetermined | Est | Unknown | 150 | Yes | Ct River | Main line under road in a tunnel became dislodged During Rain storm we Jacked the pipe back into place has minimal leaking waiting for storm water to subside so we can complete are repair.
Middletown WPCF | Middletown | 216 East Ridge | Sewage Bypass | Rain <1" per hour | 3/28/2021, 5:45 PM | 3/28/2021, 3:46 PM | Sewer Main | Yes | Raw Sewage | Sewer Line Blockage - Roots | Homeowner sewage coming out of toilet | 51 - 500 gallons | est |  | 60 | No |  | Damage to the downstairs of this house basement was finished Cleaning comp was on scene
Middletown WPCF | Middletown | 207 Westfield st | Sewage Bypass | Dry | 5/11/2021, 2:23 PM | 5/11/2021, 4:30 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | owners | 1-50 gallons | est | 1-50 gallons | 30 | No | none | student threw a stick in the manhole threw the vent hole causing papers to jam up the lateral and clogg pipe
Middletown WPCF | Middletown | behind 17 Blue grass dr. | Sewage Bypass | Dry | 6/1/2021, 2:00 PM | 6/1/2021, 3:00 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Roots | homeowner | 51 - 500 gallons | est. | n/a | 50 | No
Middletown WPCF | Middletown | Info 34 East Main st | Sewage Bypass | null | 7/9/2021, 10:30 AM | 7/9/2021, 12:45 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Staff | Undetermined | Undetermined | undetermined | 1000 | Yes | Ct River | 6.2 inch rain event
Middletown WPCF | Middletown | Info 100 River rd | Sewage Bypass | null | 7/9/2021, 10:45 AM | 7/9/2021, 12:50 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Staff | Undetermined | Undetermined | Undetermined | 1000 | Yes | Ct river | 6.2 Rain event
Middletown WPCF | Middletown | 377 Ridge Rd. middletown ct 06457 | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:00 AM | 7/9/2021, 2:15 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | home owner noticed water coming from a open pipe in basement floor. | 1-50 gallons | total volume was determined visually |  | 30 | No
Middletown WPCF | Middletown | 100 River Rd. | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 1:13 AM | 9/2/2021, 3:30 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Visual site of manhole | Undetermined |  |  | 150 | Yes | CT river.
Middletown WPCF | Middletown | intersection of Newfield st and Rose circle. | Sewage Bypass | Dry | 9/3/2021, 6:01 AM | 9/3/2021, 6:02 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | call in to our dept | 51 - 500 gallons |  |  | 60 | No
[15 empty] | 2530 |  | 2300

## MILFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Milford - Housatonic Collection System | Milford | Knob Hill Road | Sewage Bypass | Dry | 1/4/2021, 8:00 AM | 1/4/2021, 2:15 PM | Manhole | null | Raw Sewage | Unknown | phone call from resident | 1-50 gallons | estimate | 375 | 375 | No | unknown
Milford - Housatonic Collection System | Milford | 95 Meadowside Drive | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 7:11 AM | 9/2/2021, 9:00 AM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | SCADA Alarm | 1,001 - 5,000 gallons | estimate | 1,000 - 5,000 | 3000 | Yes | Atlantic Ocean | Rain flooded electrical vault submerging control panel. Septic hauler called in to pump flows initially and stop bypass. Rental pump then installed until control panel can be replaced.
Milford - Housatonic Collection System | Milford | Morningside Drive | Sewage Bypass | Rain <1" per hour | 9/9/2021, 6:00 AM | 9/9/2021, 6:30 AM | Manhole | null | Raw Sewage | Mechanical Equipment Failure | Routine inspection of emergency pumping equipment | 1-50 gallons | estimate | 1-50 gallons | 30 | No |  | The hose for the emergency pumps at Morningside Pump Station leaked some raw wastewater onto the street. We have the correct fitting to connect the emergency pumps to the force main in the valve vault. This will allow us to eliminate the hose running to the manhole.
Milford - Housatonic WPCF | Milford | Housatoninc | Sewage Bypass | Rain <1" per hour | 2/26/2021, 7:45 AM | 2/27/2021, 7:46 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | sampling the final effluent | 1-50 gallons |  |  | 30 | Yes | Housatonic | due to high flows nd snow melt solids in the final tanks got high and flowed over to the final effluent and out of the final flow. polymer was sent out for the weekend and holding of solids in the system at Housatonic as also implemented over the weekend and only lasted for a couple of hours
Milford - Housatonic WPCF | Milford | 146 High St | Sewage Bypass | Dry | 3/19/2021, 3:44 PM | 3/19/2021, 4:48 PM | Basement | Yes | Disinfected Partially Treated Raw Sewage | Sewer Line Blockage - Other | phone call from condo complex super. | 1-50 gallons | estimate of sewage on basement floor |  | 30 | No
Milford - Housatonic WPCF | Milford | 1255 Oronoque Road, Milford Ct 06461 | Sewage Bypass | Dry | 7/6/2021, 7:30 AM | 7/6/2021, 7:30 AM | Treatment Plant | No | Sludge Spill | Sewer Line Blockage - Other | Morning inspection | 1-50 gallons | estimate | 1-50 gallons | 30 | No | NA | WAS storage tank burped during aeration cycle pushing sludge onto walkway.
Milford - Housatonic WPCF | Milford | west ave | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 1:41 PM | 7/9/2021, 2:30 PM | Pump Station | No | Raw Sewage | Excessive Flows - Storm Event | flow meter zeroed out at housatonic plant | 20,001 - 50,000 gallons | estimated | n/a | 30000 | Yes | beaverbrook trail
33495

## MONTVILLE
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
MONTVILLE | Montville | 2173 CT-32, Montville, CT | Sewage Bypass | Dry | 12/14/2021, 02:00 PM | 12/14/2021, 06:00 PM | Sewer Main |  | Raw Sewage | Mechanical Equipment Failure | Operator inspection | 1000 g | Superintendent's direct inspection | 1000 g | 1000 | No | n/a | The PS was bypassed to prevent further discharges and allow for repairs. The emergency contractor B
Montville | Montville | 83 Pink Row | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 5:35 AM | 9/2/2021, 6:00 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Storm Ida forecasted. Monitoring of influent flow above design. | 50,001 - 100,000 gallons | Influent flow rate. |  | 75000 | Yes | Horton Cove then Thames River | Hurricane Ida became Tropical Storm Ida which impacted the State beginning on Sept 1 through the night with extreme rain (thus flash flooding). Plant is not CSO facility. Inflow/Infiltration led to over-design flows, low detention times in secondary treatment and chlorine contact chamber.

## NAUGATUCK
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Naugatuck WPCF | Naugatuck | 99 Cold Spring Circle | Sewage Bypass | Dry | 11/16/2021, 10:00 AM | 11/16/2021, 11:30 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | Homeowners | 51 - 500 gallons |  |  | 75 | No
Naugatuck WPCF | Naugatuck | 641 Maplewood Hill Rd | Sewage Bypass | Dry | 3/26/2021, 11:30 AM | 3/26/2021, 1:30 PM | Manhole | Yes | Raw Sewage | Sewer Line Blockage - Other | Construction operator | 51 - 500 gallons |  |  | 150 | No
Naugatuck WPCF | Naugatuck | 500 Cherry St ext | Sewage Bypass | Dry | 6/6/2021, 5:15 PM | 6/6/2021, 7:01 PM | Pump Station | No | Raw Sewage | Electrical Equipment Failure | Operator | 1,001 - 5,000 gallons |  |  | 1500 | Yes | Naugatuck River
Naugatuck WPCF | Naugatuck | 174 Prospect St | Sewage Bypass | Dry | 8/4/2021, 7:45 PM | 8/4/2021, 9:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Hiker | 501 - 1,000 gallons |  |  | 750 | Yes | Filling Mill Brook
Naugatuck WPCF | Naugatuck | 261-267 Cross St | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 7:00 AM | 9/2/2021, 9:15 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Routine check | 501 - 1,000 gallons | Wet Well level trending at plant | Possibly up to 85,000 gallons | 84000 | Yes | Beacon Hill Brook | Bypass due to very heavy rainfall. Amount is estimated from time bypass was observed.
86475

## NEW BRITAIN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
New Britain | New Britain | 142 Steele St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:00 AM | 7/9/2021, 2:30 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | ROW Sanitary bypass out of Manhole S3-176 directly into Webster Brook from heavy rain event
New Britain | New Britain | 237 Linden St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:30 AM | 7/9/2021, 2:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | Excessive flow in sanitary line caused backup, drained into nearby catch basins
New Britain | New Britain | 231 Belden St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:30 AM | 7/9/2021, 2:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | Excessive flow in sanitary line caused backup, drained into nearby catch basins
New Britain | New Britain | 233 Belden St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:30 AM | 7/9/2021, 2:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | Excessive flow in sanitary line caused backup, drained into nearby catch basins
New Britain | New Britain | 245 Belden St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:30 AM | 7/9/2021, 2:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | Excessive flow in sanitary line caused backup, drained into nearby catch basins
New Britain | New Britain | 221 Linden St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:30 AM | 7/9/2021, 2:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook | Sanitary surcharge due to rain event, excessive flow of raw sewage out of manhole in front of 221 Linden St
New Britain | New Britain | 245 Belden St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 1:55 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook
New Britain | New Britain | 231 Belden St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 2:01 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook
New Britain | New Britain | 237 Linden St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 2:04 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook
New Britain | New Britain | 16 Wildwood St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 2:07 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Webster Brook
New Britain | New Britain | 145 Steele St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 2:10 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Willow Brook
New Britain | New Britain | 183 Steele St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 12:00 AM | 9/2/2021, 2:12 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Willow Brook
New Britain | New Britain | 108 Market St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 10:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 50 | No
New Britain | New Britain | 1181 East St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 10:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Piper Brook
New Britain | New Britain | 1170 East St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 10:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Piper Brook
New Britain | New Britain | 1146 East St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 10:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Piper Brook
New Britain | New Britain | 1133 East St | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 10:00 AM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewer Crew | Undetermined | N/A | N/A | 150 | Yes | Piper Brook
2450

## NEW LONDON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
New London STP | New London | 42 Harborview Avenue New London CT | Sewage Bypass | Rain <1" per hour | 3/28/2021, 8:40 PM | 3/28/2021, 10:12 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Road Crew on call person notified by call service who was notified by home owner | 51 - 500 gallons | Tank capacity of cleanup crews vacuum | 100 gallons | No |  | 3/28/2021 2040 On call service notified road crew on call of home owners complaint. 2050 road crew on call onsite 2212 blockage cleared and sewer flowing 3/29/21 0730 clean up company onsite for basement clean up
New London STP | New London | 100 Trumbull Street New London CT | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 3:05 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | Third Shift Operator | Over 1,000,000 gallons | We estimate that about 1,093,750 gallons by converting incoming to outgoing flow to gpm. |  | Yes | Bentley Creek | The volume reported is an estimate. Please see the attached document for incident description.

## NEW MILFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
New Milford | New Milford | 48 Danbury Road New Milford, CT 06776 | Sewage Bypass | Dry | 11/30/2021, 7:25 AM | 11/30/2021, 8:30 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Police Department notified office personnel about a manhole discharging onto street. | 51 - 500 gallons | Estimated |  | Yes | Housatonic River | Crew cleared blockage with Jetter and disinfected area with Bleach. Storm drain that ultimately discharges into Housatonic River was not active with ground water at the time of incident and was flushed with bleach and water.

## NEWTOWN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Newtown WPCF | Newtown | 20 Washington Avenue | Sewage Bypass | Dry | 10/19/2021, 11:15 AM | 10/19/2021, 1:30 PM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Other | Reported by Public Works | 51 - 500 gallons | Estimate |  | Yes | Pootatuck River | It appeared paper product from the private lateral of the condominium were pushed through by roto rooter into town main manhole, which caused the back up to spread from the private manhole to the town's manhole. Jetted from flooded upstream manhole and broke stoppage. Suggested to the town to check and jet the downstream line in the near future.

## NORTH HAVEN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
NORTH HAVEN WPCF | North Haven | 25 Marion Dr, North Haven, CT | Sewage Bypass | Dry | 12/14/2021, 11:00 AM | 12/14/2021, 07:00 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Grease | Reported by resident. | Less than 100 gallons estimated at this time based on sewer shed. | Visual estimate. | Less than 100 gallons | 75 | No |  | Staff jet cleaned the line to remove grease and other debris. Staff cleaned up around the manholes
North Haven WPCF | North Haven | 22 Marlen Drive | Sewage Bypass | Dry | 4/13/2021, 8:09 AM | 4/13/2021, 9:09 AM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Grease | A local resident called to report sewage flowing from manhole to the nearest storm drain. | 1,001 - 5,000 gallons | visual estimate due to lack of flow meter |  | 3000 | Yes | Culvert to stream
North Haven WPCF | North Haven | 1122 Univeral Drive, North haven, CT | Sewage Bypass | Dry | 7/16/2021, 10:35 AM | 7/16/2021, 10:40 AM | Treatment Plant | null | Sludge Spill | Sewer Line Blockage - Other | Staff discovered bypass while loading a tanker truck for disposal purposes | 51 - 500 gallons | estimated based on visual observation | 100 gallons | 150 | No |  | While loading a tanker truck, the manhole which received drained sludge from the loading pipe started to overflow. I realized the 2 way valve valve which directs sludge to the truck or to the sewer drain line was partially open to the drain line. The sludge was very thick (6% solids), which slowed its ability to drain through the sewer pipe to the plant headworks. Staff quickly stopped the flow and isolated the spill. The sludge was pushed back into the surcharged manhole and limed.
North Haven WPCF | North Haven | 1122 Universal Drive North Haven, CT 06473 | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 10:45 AM | 7/10/2021, 12:05 AM | Sewer Main | null | Raw Sewage | Excessive Flows - Storm Event | Bypass pipe for excessive flow to plant has a flow meter | Over 1,000,000 gallons | flow meter | 3.7M gallons | 3700000 | Yes | Quinnipiac River | Tropical Storm Elsa dropped over six inches of rain on the Town of North Haven. Town notified us on 7/12/21 that flow meter showed flow had gone through the overflow bypass pipe just before the plant.
North Haven WPCF | North Haven | 1122 Universal Drive North Haven, CT 06320 | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 6:15 AM | 9/2/2021, 6:15 AM | Treatment Plant | No | Raw Sewage | Excessive Flows - Storm Event | Alarm from flow gauge sent notification that flow had entered the bypass pipe | 100,001 - 500,000 gallons | Duration of the time the pipe was full |  | 300000 | Yes | Quinnipiac River
North Haven WPCF | North Haven | 32 Cloudland Road North Haven, CT 06372 | Sewage Bypass | Other | 9/9/2021, 7:15 AM | 9/9/2021, 9:05 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Neighbor closest to manhole on morning walk saw flow coming out of holes of manhole cover | 501 - 1,000 gallons | amount of flow coming out of manhole cover |  | 750 | No |  | Grease buildup in sewer main caused blockage in line that caused a small bypass
4003975

## NORWALK
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Norwalk WPCF | Norwalk | 360 Connecticut Ave | Sewage Bypass | Dry | 9/12/2021, 12:10 PM | 9/12/2021, 12:10 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Phone call by passer by | 51 - 500 gallons | Observation |  | 300 | Yes | Keeler Brook
Norwalk WPCF | Norwalk | 365 Westport Ave | Sewage Bypass | Dry | 11/30/2021, 11:38 AM | 12/1/2021, 12:00pm | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Called in by Police and Resident | 501 - 1,000 gallons |  | 501-1,000 gallons | 800 | Yes | Keeler Brook North of I-95 | The team deployed the jet/vac truck to clear the blockage and flow was restored to the sewer line shortly after arrival. Crews returned on December 1, 2021 to CCTV the line and found a collapse in the main.
Norwalk WPCF | Norwalk | 360 Connecticut Ave. | Sewage Bypass | Dry | 7/20/2021, 1:30 PM | 7/20/2021, 1:45 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Grease | Service Request | 51 - 500 gallons |  |  | 300 | Yes | Keelers Brook
Norwalk WPCF | Norwalk | 60 south smith st 06855 | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 7/2/2021, 11:49 PM | 7/3/2021, 2:06 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Over 1,000,000 gallons | flow metering | 300000 | 300000 | Yes | Norwalk River | The Norwalk WWTF experienced a significant rain event on July 2nd and 3rd 2021 totaling 2.8 inches. The facility reached 30 MGD capacity at approximately 11:45 pm on July 2nd at which time the Storm Flow SOP was implemented. The WWTF discharged 300,000 gallons through the 002 outfall during the 2 hour event. All sampling and analysis was completed per the SOP and results and calculations will be included in the July 2021 DMR/MOR submittal.
Norwalk WPCF | Norwalk | 60 South Smith Street | NPDES Permitted Bypass of Secondary Treatment | Rain <1" per hour | 10/26/2021, 9:40 AM | 10/26/2021, 11:45 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Over 1,000,000 gallons | Flow Meter |  | 1000000 | Yes | Norwalk River | See Attached.
Norwalk WPCF | Norwalk | 60 South Smith Street | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 7/9/2021, 7:25 AM | 7/10/2021, 5:30 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Over 1,000,000 gallons |  |  | 1000000 | Yes | Norwalk River | See Attached Letter
Norwalk WPCF | Norwalk | 60 South Smith Street. Norwalk, CT 06855 | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 9/1/2021, 9:59 PM | 9/1/2021, 9:59 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Undetermined |  |  | 1000000 | Yes | Norwalk River
Norwalk WPCF | Norwalk | Smith and Wall Street | Sewage Bypass | Dry | 8/11/2021, 9:32 AM | 8/11/2021, 12:00 AM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | Contractors saw it as soon as they turned on their pump | 1-50 gallons | Visual by contractors on site |  | 30 | Yes | Norwalk River | We are lining the aged sewer main on smith and wall street today. When the contractors Green Mountain Pipe turned on their pump a seal in the pipe was missed and under fifty gallons of sewage leads out and dripped into a catch basin. Less than ten gallons is assumed to reach the basin which eventually leads to the Norwalk river.
Norwalk WPCF | Norwalk | 1 Pine Street | Sewage Bypass | Dry | 7/19/2021, 4:30 PM | 7/19/2021, 4:30 PM | Lateral - Private | No | Raw Sewage | Electrical Equipment Failure | Property management company called the city dispatch to inform. | 1-50 gallons | The dry area of the spill shows it was a small bypass, property maintenance confirmed it was definitely less than 50 gallons. |  | 30 | No |  | The property management team had Wynn River coming to work on the lateral clog and Foleys pump is coming to repair pumps that appeared to be shorted. As of 7/23/2020 the issue has been repaired and the private system is working well.
Norwalk WPCF | Norwalk | Karen Drive Pump Station | Sewage Bypass | Dry | 5/24/2021, 4:08 PM | 5/24/2021, 4:30 PM | Pump Station | null | Raw Sewage | Mechanical Equipment Failure | SCADA alarmed of a high level and our crew responded right away to find the station bypassing from a manhole in it s driveway. | 51 - 500 gallons | Visual Inspection | Not Known | 300 | No |  | Our electrician and vac truck team responded with in minutes, as all were still working finishing up their day. The SSO was quickly stopped and the mechanical problem is being resolved by our team.
Norwalk WPCF | Norwalk | 60 south smith street | Sewage Bypass | Dry | 7/15/2021, 10:30 AM | 7/15/2021, 10:30 AM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | Plant Staff | 1-50 gallons |  |  | 30 | No |  | MCVac a contractor of ours was offloading a grit and sewage load from our headwork's area and aproximentally 50 gallons left the septage receiving area. The spill was cleaned by mcvac and our collections crew right away. Spill happened less than one minute.
Norwalk WPCF | Norwalk | 60 South Smith Street | Sewage Bypass | Dry | 8/3/2021, 9:00 AM | 8/3/2021, 12:00 PM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | Happened in front of inland water crew | 51 - 500 gallons | Visual |  | 300 | No |  | Inland Waters was emptying truck and had a spill that breached the containment area. Inland waters cleaned the area immediately
Norwalk WPCF | Norwalk | 10 Peter Avenue | Sewage Bypass | Rain <1" per hour | 3/18/2021, 10:30 PM | 3/18/2021, 11:00 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Local water company noticed manhole leaking and called it in. | 51 - 500 gallons |  |  | 300 | No
Norwalk WPCF | Norwalk | 4 Mark Drive, Norwalk | Sewage Bypass | Dry | 3/8/2021, 10:30 AM | 3/8/2021, 12:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Norwalk DPW crew member noticed a manhole overflowing at 4 Mark Drive. | 51 - 500 gallons | Handbook |  | 300 | No
Norwalk WPCF | Norwalk | 11 Charles Street | Sewage Bypass | Dry | 1/3/2021, 4:15 PM | 1/3/2021, 4:15 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | Home Owner Called in for basement flooding | 51 - 500 gallons | Pictures of spill in homeowners basement |  | 300 | No |  | Collections on-call team responded and found a surcharged manhole. The homeowner shared pictures of her basement. The team jetted the line and restored flow to the mainline and the lateral of the effected homeowner. Our collections team will revisit the area tomorrow for a full inspection and cleaning.
Norwalk WPCF | Norwalk | 66 Grandview Ave | Sewage Bypass | Dry | 10/19/2021, 11:00 AM | 10/19/2021, 11:00 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | The resident called in a sewage back-up but never said they had any in the basement until he was contacted by SUEZ the next morning. | Undetermined |  |  | 25 | No
Norwalk WPCF | Norwalk | 44 Orchard Street | Sewage Bypass | Dry | 2/23/2021, 8:30 AM | 2/26/2021, 6:00 PM | Sewer Main | null | None | Sewer Line Blockage - Other | Norwalk DOT took a complaint for a sinkhole and realized it was a collapsed 24" gravity main. | Undetermined |  |  | 300 | No |  | The cities 24" gravity main has collapsed and caused erosion around the collapse creating a sink hole in the street at 44 Orchard ave. Norwalk. When have shut down the road and have an emergency contractor in route. Sewage never left the sink hole at the bottom of pipe was in tact and the conveyance of sewage remained or returned to the intact 24" main for travel to the WPCF for treatment.
Norwalk WPCF | Norwalk | 250 westport ave | Sewage Bypass | Dry | 3/2/2021, 12:27 PM | 3/2/2021, 12:45 PM | null | null | Raw Sewage | Sewer Line Blockage - Other |  | 51 - 500 gallons |  |  | 300 | No
Norwalk WPCF | Norwalk | 34 dairy Farm Road | Sewage Bypass | Dry | 4/14/2021, 1:35 PM | 4/14/2021, 2:00 PM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Other | Dye testing | 1-50 gallons |  |  | 30 | No |  | The City and Homeowner are currently working together to find a solution to the leaking lateral. The lateral is private and owned by the home owner at 34 Dairy Farm Road. Our Collections team has responded to clean any sewage spilled up and to assist homeowner whole a repair is made.
Norwalk WPCF | Norwalk | Marshall, North Water | Sewage Bypass | Dry | 5/25/2021, 3:15 PM | 5/25/2021, 3:45 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Collections Team noticed it whole doing rounds | 51 - 500 gallons | Visual Inspection |  | 300 | No
Norwalk WPCF | Norwalk | 32 Douglas Dr. Norwalk, Ct | Sewage Bypass | null | 6/1/2021, 7:50 AM | 6/1/2021, 8:15 AM | null | null | Raw Sewage | Sewer Line Blockage - Other |  | 51 - 500 gallons |  |  | 300 | No
Norwalk WPCF | Norwalk | 110 Patrick Avenue | Sewage Bypass | Rain <1" per hour | 2/15/2021, 12:34 PM | 2/15/2021, 1:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Roots | SNEW a local utility was working in area and saw the manhole overflowing | 51 - 500 gallons |  |  | 50 | Yes
NORWALK WPCF | Norwalk | 21 Poplar St, Norwalk, CT | Sewage Bypass | Dry | 12/20/2021, 08:30 AM | 12/20/2021, 08:45 PM | Basement |  | Raw Sewage | Unknown | Resident Called customer service. | Less than 50 gallons | Complainant information. | Less than 50 Gallons | 30 | No |  | Flow was restored to the main line and back-up was eliminated.
Norwalk WPCF | Norwalk | Building #5 Gillies Lane | Sewage Bypass | Dry | 4/28/2021, 2:45 AM | 4/28/2021, 2:45 PM | Manhole | null | Raw Sewage | Unknown | Resident Called In | 1-50 gallons | Visual Inspection |  | 30 | No |  | Manhole was hard to find. When found we had to mobilize a sump and vac truck to clear the line. The line was cleaned and cleared. Our collections team will return 4/28/21 for a CCTV inspection.
3304355

## NORWICH
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Norwich WPCF | Norwich | 16 South Golden Street. | Sewage Bypass | Dry | 10/14/2021, 12:51 PM | 10/14/2021, 1:14 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other | Customer Call | 501 - 1,000 gallons | Visual Estimate |  | 750 | Yes | Ford Brook
Norwich WPCF | Norwich | 16 S Golden St | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 5:30 AM | 9/2/2021, 7:30 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | Operators at plant during storm event | 20,001 - 50,000 gallons | Visual estimate of GPM Times duration of flow | 24,000 estimate | 24000 | Yes | Ford Brook | Splitting box from Aeration Tanks to Final clarifiers leaking out of concrete containment
Norwich WPCF | Norwich | 45 Salem turnpike | Sewage Bypass | Dry | 9/30/2021, 1:32 PM | 9/30/2021, 2:30 PM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Grease | Customer call | 1-50 gallons | Visual Estimate |  | 30 | Yes | Ford Brook
Norwich WPCF | Norwich | 8 City Landing | Sewage Bypass | Dry | 1/1/2021, 4:55 PM | 1/1/2021, 5:45 PM | Pump Station | null | Raw Sewage | Sewer Line Blockage - Grease | Notification from meter | Undetermined |  |  | 150 | Yes | Shetucket river
Norwich WPCF | Norwich | 5 8th street Norwich CT | Sewage Bypass | Dry | 9/30/2021, 12:36 PM | 9/30/2021, 1:05 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Roots | Employee call in | 5,001 - 20,000 gallons | Calculated estimate | 6000 | 6000 | Yes | Shetucket river
Norwich WPCF | Norwich | 84 Hamilton Ave | Sewage Bypass | Rain <1" per hour | 2/19/2021, 3:50 PM | 2/19/2021, 5:00 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Resident called NPU emergency number | 501 - 1,000 gallons | Visual observation | 700 Gal, estimated 10 gal/min for a duration of 70 mins, Rags was determined to be the cause, small amount of grease, 2/5ths of a 5gallon paill | 700 | Yes | Shetuckett River
Norwich WPCF | Norwich | Crown St | Sewage Bypass | Dry | 1/18/2021, 2:25 PM | 1/18/2021, 2:25 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | inspection of metered manhole | 20,001 - 50,000 gallons |  |  | 30000 | Yes | Thames River
Norwich WPCF | Norwich | 190 South Thames Street | Sewage Bypass | Dry | 10/7/2021, 1:00 PM | 10/7/2021, 1:05 PM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | Leaking Seal while preforming | 1,001 - 5,000 gallons | CSO flow meter | 1986 | 1986 | Yes | Thames River
NORWICH WPCF | Norwich | 38 Main St, Norwich, CT | Sewage Bypass | Dry | 12/29/2021, 12:15 PM | 12/29/2021, 12:15 PM | Sewer Main |  | Raw Sewage | Unknown | Called in by Norwich Marina caretaker | 235GPM when haulers not pumping.75,273 Gallons Discharged | Unable to determine exact amount due to the inflow of river water being pumped with the sewage. Sew |  | 75273 | Yes | Thames River
Norwich WPCF | Norwich | 17 South Thames ST, Norwich CT | Sewage Bypass | Dry | 7/29/2021, 12:00 PM | 7/29/2021, 1:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Call from contractor | 51 - 500 gallons | Flow Meter from CSO | 305 gallons | 305 | Yes | Thames River
Norwich WPCF | Norwich | 190 South thames St | Sewage Bypass | Dry | 9/11/2021, 7:13 PM | 9/12/2021, 12:00 AM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | testing force main | 20,001 - 50,000 gallons | Calculated estimate | 35000 | 35000 | Yes | Thames River
Norwich WPCF | Norwich | 70 Thames Street | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 3:20 AM | 9/1/2021, 7:19 AM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | Plant inspection | 100,001 - 500,000 gallons | Calculated Pump station output | 286800 | 286800 | Yes | Thames River
Norwich WPCF | Norwich | 44 Falls Ave, Norwich CT | Sewage Bypass | Dry | 7/30/2021, 8:00 AM | 7/30/2021, 11:45 AM | Sewer Main | null | Raw Sewage | Unknown | during morning rounds at the plant we noticed the line leaking | Undetermined | Visual estimate | >5,000 gal | 5000 | Yes | Yantic River
Norwich WPCF | Norwich | 10 North Thames St. | Sewage Bypass | Dry | 8/5/2021, 3:00 AM | 8/5/2021, 11:45 PM | Sewer Main | No | Raw Sewage | Unknown | Employee daily rounds | 50,001 - 100,000 gallons | Visual estimate | 65625 | 65625 | Yes | Yantic River | I did a 2-hour report the other day, while checking over the report I see it submitted an end time that was not correct. Will email Ann Straut to notify.
Norwich WPCF | Norwich | 10 North Thames St. | Sewage Bypass | Dry | 8/7/2021, 11:04 AM | 8/7/2021, 11:14 AM | Sewer Main | No | Raw Sewage | Unknown | Witness | 51 - 500 gallons | Visual estimate | 475 | 475 | Yes | Yantic River
Norwich WPCF | Norwich | 385 N Main St. Norwich | Sewage Bypass | Dry | 1/30/2021, 5:40 AM | 1/30/2021, 5:40 AM | Manhole | No | Raw Sewage | Unknown | meter notification alert | Undetermined | there was no overflow | 0 gallons | 0 | No |  | FAS meter notification came in at 7:43 AM for CSO #23 overflow, conducted visual inspection and there was no evidence that there was or had been an overflow
Norwich WPCF | Norwich | 5 8th street Norwich CT | Sewage Bypass | Dry | 10/17/2021, 9:30 AM | 10/17/2021, 10:20 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Customer call | 51 - 500 gallons |  |  | 300 | No
Norwich WPCF | Norwich | 78 Washington Street Norwich CT | Sewage Bypass | Dry | 10/17/2021, 9:30 AM | 10/17/2021, 10:20 AM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Customer call | 51 - 500 gallons |  |  | 300 | No
Norwich WPCF | Norwich | 44 Falls Ave Norwich CT | Sewage Bypass | Dry | 10/8/2021, 5:00 AM | 10/8/2021, 6:55 AM | Treatment Plant | null | Sludge Spill | Unknown | Called by sludge hauling company | Undetermined | Dry sludge cake approximately 3 cubic yards | 3 cubic yards | 20 | No |  | New driver for sludge hauling company lifted roll off container at too great an angle and dumped approximately 3 cubic yards of roughly 15% solids sludge cake
Norwich WPCF | Norwich | 18 Old Salem Road | Sewage Bypass | Dry | 2/12/2021, 8:00 AM | 2/12/2021, 8:45 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Resident Called to inform | 51 - 500 gallons | visual inspection | 250 gal. | 250 | No |  | visual inspection of flow 3gal/min for 45 min. catch basin had 112 gal inside calculated, jetted main/vacuumed catch basin, cleaned area, 5 gal of rags
Norwich WPCF | Norwich | 365 Boswell Ave. | Sewage Bypass | Dry | 7/13/2021, 3:25 PM | 7/13/2021, 4:10 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Called in | 51 - 500 gallons | visual estimate |  | 300 | No
Norwich WPCF | Norwich | 190 South Thames Street | Sewage Bypass | Dry | 8/27/2021, 12:56 PM | 8/27/2021, 1:02 PM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | Customer Call | 1-50 gallons | Visual estimate |  | 30 | No |  | Replaced weeping gasket on temporary force main.
Norwich WPCF | Norwich | 16 South Golden St. | Sewage Bypass | Dry | 8/29/2021, 11:11 AM | 8/29/2021, 12:37 PM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | Customer Called | 51 - 500 gallons | Visual Estimate | 100 | 100 | No |  | Had a leaking gasket on temporary main, used vac truck to suck while changing gasket.
Norwich WPCF | Norwich | 10 South Thames St. | Sewage Bypass | Dry | 8/8/2021, 7:04 PM | 8/8/2021, 7:15 PM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | customer called | 1,001 - 5,000 gallons | Calculated estimate | 2500 | 2500 | No |  | Hole in bypass pumping hose. Changed section of pipe.
Norwich WPCF | Norwich | 16 South Golden St. | Sewage Bypass | Dry | 9/11/2021, 3:55 PM | 9/11/2021, 6:02 PM | Sewer Main | No | Raw Sewage | Mechanical Equipment Failure | Customer Call | 501 - 1,000 gallons | Visual estimate | 600 | 600 | No
Norwich WPCF | Norwich | 70 South Thames St. | Sewage Bypass | Rain <1" per hour | 9/9/2021, 7:42 AM | 9/9/2021, 11:16 AM | Sewer Main | null | Raw Sewage | Mechanical Equipment Failure | Customer Email | 51 - 500 gallons | Visual Estimate | 350 | 350 | No
536844

## ORANGE
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Orange WPCA | Orange | Old Lambert Road | Sewage Bypass | Dry | 6/17/2021, 3:00 PM | 6/18/2021, 8:00 AM | Sewer Main | null | Raw Sewage | Unknown | Notified by Robert Britain of the Town of Orange CT @ 1500 on 6/17/2021 | 5,001 - 20,000 gallons | Using pump trends that feed broken force main | 12,118 gallons (Max amount assuming all flow left the main at the break) | Yes | Unknown stream approximately 3 feet wide and 100 yards from Old Lambert Road in Orange CT

## OXFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
OXFORD | Oxford | 46 Towner Ln, Oxford, CT | Sewage Bypass | Rain less than 1" per hour | 12/30/2021, 02:30 PM | 12/31/2021, 12:15 PM | Sewer Main |  | Raw Sewage | Other | WPCA staff during check of station | Under 10,000 gallons | By the amount of time and by the average discharge of the station | 12,500 gallons | Yes | Little River | A repair coupling was placed on the force main were a 1 inch hole what is found.

## PLAINFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Plainfield | Plainfield | 21 Brookside Dr Plainfield, CT 06374 | Sewage Bypass | Dry | 3/19/2021, 3:00 AM | 3/19/2021, 7:30 AM | Pump Station | null | Raw Sewage | Mechanical Equipment Failure | zero flow going to sewage treatment plant | 20,001 - 50,000 gallons | estimation: took the total plant flow from the previous day and estimated what 4 hours of flow would be. |  | 30000 | Yes | Horse Brook | The pump station lost power around 1:45am on 3/19/21 and the generator kicked on. Around 3:00 am on 3/19/21 the flow chart at the Village Treatment Plant indicated no flow entering the plant. An incident caused all three sewage pumps to lose prime causing the bypass. All pumps were primed and back online around 7:30 am. It did not look like the bypass made it to the brook, but it is possible.
Plainfield | Plainfield | 50 Birch street | Sewage Bypass | Dry | 5/18/2021, 10:00 AM | 5/21/2021, 8:00 AM | Treatment Plant | null | None | Mechanical Equipment Failure |  | 50,001 - 100,000 gallons |  |  | 300000 | No |  | 1 of 2 secondary tanks offline for routine maintenance.
Plainfield | Plainfield | 50 Birch street | Sewage Bypass | Dry | 5/25/2021, 11:11 AM | 5/25/2021, 11:11 AM | Treatment Plant | null | None | Mechanical Equipment Failure |  | 5,001 - 20,000 gallons |  |  | 10000 | No |  | Sludge thickening tank pumped out into aeration tank for routine maintenance.
Plainfield | Plainfield | 4 6th Street, Plainfield CT | Sewage Bypass | Dry | 5/30/2021, 10:00 AM | 6/1/2021, 3:00 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | homeowner called WPCA | 51 - 500 gallons | estimation |  | 300 | No
Plainfield | Plainfield | 20 Park Ave, Plainfield, CT 06374 | Sewage Bypass | Dry | 6/15/2021, 11:37 AM | 6/16/2021, 12:30 AM | Lateral - Public | No | Raw Sewage | Mechanical Equipment Failure | complaint | 51 - 500 gallons | estimation |  | 300 | No |  | Sewage was coming up from a small wet well at the Plainfield Little League,20 Park Ave, Plainfield, CT 06374.
PLAINFIELD NORTH WPCF | Plainfield | 333 N Main St, Plainfield, CT | Sewage Bypass | Dry | 12/22/2021, 04:30 PM | 12/22/2021, 05:30 PM | Manhole |  | Raw Sewage | Mechanical Equipment Failure | town resident | 200-400 gallons | rough estimate based on visual | About 300 gallons | 300 | Yes | Moosup River | pumps at the station were run in hand to bring wet well level down and then the relays were changed
Plainfield North WPCF | Plainfield | 1 Unity Dr, Moosup, CT 06354 | Sewage Bypass | Rain <1" per hour | 5/5/2021, 10:30 AM | 5/5/2021, 10:40 AM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Other | could not flush toilet | 1-50 gallons | estimation |  | 10 | No |  | A private lateral was blocked with excess paper products. Blockage was relieved and pitch of pipe was changed to prevent future blockages.
PLAINFIELD, TOWN OF | Plainfield | 333 N Main St, Plainfield, CT | Sewage Bypass | Dry | 12/10/2021, 02:00 PM | 12/10/2021, 02:30 PM | Manhole |  | Raw Sewage | Mechanical Equipment Failure | phone call from resident | 50-100 gallons | rough estimation by sight | 50-100 gallons | 75 | No |  | pump station pumps ran in manual to bring wet well level down and the mechanical issue was resolved.
340985

## PLYMOUTH
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Plymouth WPCF | Plymouth | 35 Canal St | Sewage Bypass | Dry | 1/8/2021, 8:30 AM | 1/8/2021, 8:32 AM | Treatment Plant | null | Sludge Spill | Unknown | Truck driver notified operator | 1-50 gallons | estimated | approximately 5-10 gallons | 10 | No |  | Operator was filling sludge tanker and tanker got over filled. When tanker driver drove up the driveway some sludge spilt out.
Plymouth WPCF | Plymouth | 783 main st, plymouth ct | Sewage Bypass | Other | 2/1/2021, 11:45 AM | 2/1/2021, 2:30 PM | Manhole | null | Raw Sewage | Unknown | homeowner notified WPCA that there was sewage in the woods near his house | Undetermined |  | volume unkown. Sewage was slowly seeping out of the ground where a buried manhole was in an easement that goes through the woods | 150 | Yes | There is a small brook near the area | Plant personal responded to blockage immediatley. Bloackage took a little longer to clear due to winter storm and the fact that confined space entry was needed
Plymouth WPCF | Plymouth | Canal St | Sewage Bypass | Dry | 3/30/2021, 11:00 AM | 3/30/2021, 11:15 AM | Treatment Plant | null | Sludge Spill | Mechanical Equipment Failure | Plant Operator | 1-50 gallons | estimated | less than 5 gallons | 5 | No |  | Sludge Tanker was leaving and vent on tanker truck popped open. Some sludge spilled out. Sludge was hosed and cleaned. . No sludge entered basins.
Plymouth WPCF | Plymouth | lake plymouth blvd | Sewage Bypass | Dry | 4/26/2021, 7:19 PM | 4/27/2021, 11:45 AM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other | called in by resident | Undetermined |  | unknown | 300 | Yes | trickling into catchbasin | There was a pencil size hole in the force main. Sewage was seeping out of ground and some entered catch basin. Most of the sewage trickled into wooded area. Force main repair was completed 4/27
465

## PUTNAM
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Putnam | Putnam | 4 kennedy drive | Sewage Bypass | Dry | 10/29/2021, 7:54 AM | 10/29/2021, 10:58 AM | Treatment Plant | null | None | Mechanical Equipment Failure | dialey observations | 0 |  |  | 0 | No |  | secondary clearifier takin offline due to oil leakage
Putnam | Putnam | 37 Flagg Street | Sewage Bypass | Dry | 10/31/2021, 10:00 AM | 10/31/2021, 11:00 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Roots | homeowner | 1-50 gallons | estimated |  | 50 | No
Putnam | Putnam | 180 Recreation Park Road | Sewage Bypass | Dry | 3/11/2021, 11:37 AM | 3/11/2021, 12:48 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | homeowner | 1-50 gallons | estimated | n/a | 50 | No
Putnam | Putnam | 68 Florence Street | Sewage Bypass | Dry | 8/12/2021, 3:16 PM | 8/12/2021, 4:18 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Homeowner | 1-50 gallons | estimated | n/a | 50 | No | n/a

## RIDGEFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Ridgefield - Collection System | Ridgefield | 103 Danbury Road Ridgefield CT. | Sewage Bypass | Dry | 6/3/2021, 8:00 PM | 6/3/2021, 8:30 PM | Lateral - Private | Yes | Raw Sewage | Sewer Line Blockage - Grease | We were notified by plumbing company | 1-50 gallons | Visual estimate |  | 30 | No |  | We were called by a plumber who explained the problem with some store having a backup. We opened the downstream manhole that their lateral ties into and noticed it was running slowly so we cleaned the line with our vector truck.
Ridgefield - Main | Ridgefield | 22 South Street | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 11:30 PM | 9/2/2021, 12:44 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | Operator at facility noticed it. | Undetermined |  |  | 250000 | Yes | The Great Swamp | Due to the remnants of tropical storm Ida the facility was inundated excessive high flows causing the influent manhole to overflow and the influent building rear distribution box.

## SEYMOUR
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Simsbury WPCF | Seymour | 106 Meadow St. Seymour ,CT | Sewage Bypass | Dry | 3/26/2021, 12:40 PM | 3/26/2021, 1:30 PM | Basement | null | Raw Sewage | Sewer Line Blockage - Grease | crack in homeowners plumbing | 1-50 gallons | Homeowner and plumbers determined est volume . |  | No | N/A | Relieved blockage of grease and rags from manhole at Garden St. and Rt.67 Intersection.

## SHELTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Shelton | Shelton | 10 Silva Drive | Sewage Bypass | Dry | 1/12/2021, 8:00 AM | 1/12/2021, 9:00 AM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | Bubbling manhole reported | 1-50 gallons | Visual |  | No |  | Jetted line, cleaned main line of rags and debris.
Shelton | Shelton | 1 Trap Falls Road | Sewage Bypass | Other | 2/4/2021, 11:00 AM | 2/4/2021, 1:00 PM | Lateral - Public | null | Raw Sewage | Sewer Line Blockage - Other | Property owner called due to smell in building. | 1-50 gallons | Visual |  | No |  | Line runs in front of building. Minimal amount entered a drainage ditch. Jetted 300 feet of public lateral on private property, cleaned line of flushable wipes and debris.

## SIMSBURY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Simsbury WPCF | Simsbury | 570 Hopmeadow Street | Sewage Bypass | Rain <1" per hour | 5/4/2021, 12:10 PM | 5/4/2021, 12:30 PM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Other | Call from State DOT | 1-50 gallons | estimate |  | No |  | Private system owned by Dyno Nobel
Simsbury WPCF | Simsbury | 32 Whitewater Turn Simsbury Ct 06070 | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 9:50 AM | 9/2/2021, 10:00 AM | Basement | Yes | Raw Sewage | Excessive Flows - Storm Event | By Homeowner | 1-50 gallons | Guess |  | No | None | Syphon under Farmington River surcharged with excessive flow from rainfall.

## SOMERS
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Somers WPCF | Somers | 33 Quality Ave. | Sewage Bypass | Dry | 5/18/2021, 3:05 PM | 5/13/2021, 4:45 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Mechanical Equipment Failure | eColi exceedance | 5,001 - 20,000 gallons | Flow meter | unknown | Yes | Scantic River | Continued faulty UV system. Zoom meeting scheduled w/ DEEP on 5/19/21 to discuss alternative treatment.

## SOUTH WINDSOR
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
South Windsor | South Windsor | 105 Abbe Rd | Sewage Bypass | Dry | 1/6/2021, 1:56 PM | 1/8/2021, 2:00 PM | Lateral - Private | No | Raw Sewage | Unknown | Home owner reported issue | 51 - 500 gallons | By measuring the area of the puddle and estimating household water use |  | 150 | No |  | The homeowner called regarding a puddle surrounding a valve box in their yard. It was determined to be wastewater. This property is on a lower pressure system. It is unknown at this point whether the issue is part of the homeowners system or owned by South Windsor. It appears to be a faulty valve. Environmental Services Inc will be on site tomorrow, January 7, to make a repair. Update: It turns out this was a private lateral, repair has been made.
South Windsor | South Windsor | 1 Vibert Rd, South Windsor, CT 06074 | Sewage Bypass | null | 10/25/2021, 11:40 AM | 10/25/2021, 11:50 AM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | We saw it happening | 1,001 - 5,000 gallons | Estimated | Exact number unknown, guessing around 1500 gallons or so | 1500 | No |  | While performing maintenance at headworks a sluice gate accidentally triggered to close. This held back flow on Vibert Road. When the issue was discovered and the gate was fully opened back up the flow overwhelmed the wet well. All three influent pumps came on at the same time and overwhelmed the primary splitter box, so some raw influent water spilled over and onto the grass.
SOUTH WINDSOR | South Windsor | 1 Vibert Rd, South Windsor, CT | Sewage Bypass | Dry | 12/10/2021, 07:45 AM | 12/10/2021, 08:30 AM | Treatment Plant |  | Sludge Spill | Mechanical Equipment Failure | Operator that was nearby was alerted by the driver | Approximately 50 gallons of watered down thickened waste activated sludge. | Visually | About 50 gallons | 50 | Yes | A small stream that eventually ends up in the Connecticut River | We used a vac truck to suck up the sludge and put it back through headworks, the residual on the gro
South Windsor | South Windsor | 1 Vibert Road South Windsor Connecticut | Sewage Bypass | Other | 7/6/2021, 10:55 PM | 7/7/2021, 1:15 AM | Treatment Plant | null | Raw Sewage | Electrical Equipment Failure | We had to move off commercial power for Eversource to fix an electrical line | 50,001 - 100,000 gallons | It took our UV system 10 minutes to come back to full strength so we calculated that along with current flow rate. | 60000 gallons | 60000 | Yes | Connecticut River | A tree limb was down on a wire leading into the plant. We needed to move off commercial power to generator power in order for Eversource to make the repair. UV temporarily shuts down and takes about 10 minutes to warm back up so during that time we were not fully disinfecting the final effluent. This was not raw sewage but treated effluent not properly disinfected.
South Windsor | South Windsor | 1 Vibert Road, South Windsor, Connecticut 06074 | Sewage Bypass | Rain 1-2" per hour | 7/7/2021, 6:45 PM | 7/7/2021, 6:55 PM | Treatment Plant | null | Raw Sewage | Electrical Equipment Failure | We had to transfer to generator power at the plant due to trees on wires | 50,001 - 100,000 gallons | 37000 gallons. By looking on SCADA trends at how long UV was down and what flow we had moving through the plant | 37000 gallons | 37000 | Yes | Connecticut River | The flow rate was 5.3 MGD so this 10 minute bypass equaled about 37000 gallons of treated, but not fully disinfected effluent. We had to transfer to generator power so Eversource crews could fix the line coming into the plant. When we do this UV goes down and takes 10 minutes for bulbs to ramp back up to full strength. During this time we are not fully disinfecting. This bypass was not raw sewage but treated effluent that was not fully disinfected.
South Windsor | South Windsor | 1 Vibert Rd South Windsor CT 06074 | Sewage Bypass | Rain <1" per hour | 7/8/2021, 6:20 PM | 7/8/2021, 6:30 AM | Treatment Plant | null | Raw Sewage | Electrical Equipment Failure | We had to move from generator power back to commercial power and UV shut down temporarily. | 20,001 - 50,000 gallons | It takes 10 minutes for UV to come back to full strength after a shut down and we were flowing 4.2 MGD. | Around 29000 gallons | 29000 | Yes | Connecticut River | This bypass was treated effluent that was not fully disinfected, it was not raw sewage.
South Windsor | South Windsor | 1 Vibert Rd | Sewage Bypass | Rain 1-2" per hour | 8/19/2021, 10:27 AM | 8/19/2021, 10:30 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | We could see wastewater coming out of the primary clarifiers. | 1,001 - 5,000 gallons | Estimated based on what it looked like and duration. | Unknown final quantity but certainly less than 5000 gallons | 3000 | No |  | When a third influent pump came on it overwhelmed the primary clarifiers for a few minutes until we were able to make adjustments. There is no way to determine the exact amount of flow since it was only a small portion of the flow going to the primaries and for a very short time.
South Windsor | South Windsor | 445 Benedict Drive, South Windsor, CT 06074 | Sewage Bypass | Rain <1" per hour | 8/22/2021, 2:45 PM | 8/22/2021, 3:10 PM | Pump Station | null | Raw Sewage | Electrical Equipment Failure | We responded to an RTU Communications Alarm and found the PLC not working and no pumps running | 20,001 - 50,000 gallons | The station operates at 1130 gpm and the pumps stopped running for 20 mintues | Unknown but estimate around 28000 gallons | 28000 | Yes | Avery Brook | There was a power surge that destroyed the battery backup for the PLC which caused the PLC and pumps to shut down. We responded immediately.
South Windsor | South Windsor | 115 Pine Tree Lane, South Windsor, CT 06074 | Sewage Bypass | Rain <1" per hour | 8/22/2021, 3:00 PM | 8/22/2021, 4:30 PM | Basement | No | Raw Sewage | Electrical Equipment Failure | Owner found raw sewage in basement | 1,001 - 5,000 gallons | Estimating basement square footage with 6" of water on the floor | About 2200 gallons | 22000 | Yes | Avery Brook | The PLC at a pump station shut down because the battery backup died. By the time we got there the basement was already flooded.
180700

## SOUTHINGTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Southington | Southington | 781 South Main Street | Sewage Bypass | Dry | 1/12/2021, 11:30 AM | 1/12/2021, 12:30 PM | Lateral - Private | Yes | Raw Sewage | Sewer Line Blockage - Grease | Wells Fargo bank called Southington Police Department to report a sewer backup. | 1-50 gallons |  |  | 30 | No
Southington | Southington | 999 Meriden-Waterbury Turnpike | Sewage Bypass | Dry | 1/5/2021, 2:00 PM | 1/5/2021, 3:15 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Grease | Southington WPC was notified that there was water coming out of a manhole. | 1-50 gallons |  |  | 30 | No | Kiari Williams
SOUTHINGTON | Southington | 493 South End Rd, Southington, CT | Sewage Bypass | Dry | 12/2/2021, 12:00 PM | 12/2/2021, 02:00 PM | Sewer Main |  | Raw Sewage | Sewage Line Blockage - Grease | Business noticed water coming out of two manholes in parking lot. Water had also entered the buildin | 50-100 gallons | Estimate | 50-100 gallons | 300 | No |  | Jet to break blockage caused by grease in the line.
Southington | Southington | 28 Beecher Street | Sewage Bypass | Dry | 2/3/2021, 7:00 PM | 2/3/2021, 7:40 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Resident noticed water in their basement. | 1-50 gallons | Estimate |  | 30 | No
Southington | Southington | 126 Pondview Drive | Sewage Bypass | Dry | 8/24/2021, 8:45 PM | 8/24/2021, 9:05 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Resident called Southington Police Department | 1-50 gallons | Estimate |  | 30 | No |  | A resident noticed water coming out of a manhole in their yard and called the Southington Police Department. The Southington Police Department called the emergency on-call Southington Water Pollution Control Operator and the operator found the sewer main was blocked. The operator relieved the blockage to let the water flow.
Southington | Southington | 999 Meriden-Waterbury Turnpike | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 3:00 AM | 9/2/2021, 6:00 AM | Treatment Plant | null | None | Excessive Flows - Storm Event |  | 1,001 - 5,000 gallons | Estimate |  | 3000 | Yes | Quinnipiac River | The Water Pollution Control Facility received an unusual amount of rain water. All of water went through preliminary, primary, secondary, biological, and nitrification processes. Some of the water was then bypassed to an emergency storage tank. Eventually the emergency storage tank reached max capacity and water was released to the Quinnipiac River. This released water did not receive treatment for denitrification, phosphorus removal, or disinfection.
3420

## STAFFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Stafford | Stafford | 87 West Stafford Road | Sewage Bypass | Dry | 6/7/2021, 12:00 PM | 6/7/2021, 1:30 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other | DPW Worker noticed water coming from manhole | 501 - 1,000 gallons | guess | ? | 750 | No |  | Plug up was from wipes built up in the manhole drop
Stafford | Stafford | 11 Willington Ave Stafford Springs | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 12:34 PM | 7/9/2021, 8:45 PM | Sewer Main | null | Raw Sewage | Excessive Flows - Storm Event | business owner contacted WPCF | 1,001 - 5,000 gallons | guess |  | 3000 | Yes | Willimantic River | The road was dug up to investigate for a break but nothing was found. We believe water had escaped from the joints of the pipe and also the manhole. There is no way to determine flow at that location.

## STAMFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Stamford | Stamford | Washington Blvd. | Sewage Bypass | Dry | 10/8/2021, 12:00 PM | 10/8/2021, 12:40 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Grease | Reported to WPCA from local City Department | 1-50 gallons | Wetted area was estimated | Unknown | 50 | No | No | 8" sewer line was blocked from grease buildup.
Stamford | Stamford | Virgil ST. | Sewage Bypass | Dry | 11/17/2021, 8:30 PM | 11/17/2021, 9:00 PM | Manhole | Unknown at this time | Raw Sewage | Sewer Line Blockage - Grease | Fire Department notified Stamford WPCA | 1-50 gallons | Wetted area was estimated. |  | 50 | No
STAMFORD | Stamford | 79 Givens Ave, Stamford, CT | Sewage Bypass | Dry | 12/13/2021, 08:30 AM | 12/29/2021, 01:00 PM | Sewer Main |  | Raw Sewage | Other | Via dye testing and water quality sampling activities by a third party. | Estimated leak discharge rate is in a range of 0.25 to 0.5 gal. per hour | Wastewater flow conditions occurring above the stormwater pipe are low and dye dispersed into the st | Unknown length of time of leak so total volume unknown | 25200 | No |  | Repair was completed today (12/29/21)@ 1 p.m. Replaced approximately 40 LF of 8” tile sewer pipe wit
Stamford | Stamford | 111 Harbor View At the treatment plant. | Sewage Bypass | Dry | 2/10/2021, 10:00 AM | 2/24/2021, 7:00 AM | Treatment Plant | No | Raw Sewage | Unknown | 42" plant force main has a leak. Plant is under a project upgrade and excavation is going on around the force main. The excavation site filled up with raw sewage from force main. | 5,001 - 20,000 gallons | Estimated the flow of wastewater running into storm drain as 150 gpm for one hour. 9,000 total gallons. |  | 9000 | Yes | Stamford Harbor - East Branch | The leak was contained in less than an hour by using the spoils of the excavation to create a berm. The force main has a crack in it and will need to have the section of pipe replaced. Repairs are expected to be completed by 2/24/21. The plant is under construction and a temporary force main had already been installed and in use when the leak to this force main was discovered. Any leakage coming from the leaking force main is being pumped into a nearby sanitary sewer.
Stamford | Stamford | 111 Harborview Avenue | Sewage Bypass | Dry | 4/13/2021, 9:30 PM | 4/13/2021, 9:36 PM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | Operator discovered on rounds. | 5,001 - 20,000 gallons | Estimating the amount of water flowing from distribution box down the storm drain. | same | 10000 | Yes | East Branch of Stamford Harbor, Long Island Sound. | Stamford WPCA attempted to report SSO several times over the last two days but could not access the Arc-Gis reporting system. Reported the overflow to members of DEEP, Aqua Culture, and an exceedance email blast to all local authorities.
Stamford | Stamford | 1864 Summer ST. | Sewage Bypass | Dry | 5/20/2021, 11:00 AM | 5/20/2021, 12:13 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | Dye testing activities verified a leak from the sanitary sewer line is entering a below ground stormwater conveyance system. | 1-50 gallons | Visual estimated |  | 30 | Yes | Rippowam | A small leak from a sewer line will be temporarily patch from the bottom via an existing stormwater manhole structure sitting below the pipe. Long-term repair of sanitary sewer line for this section are being reviewed.
Stamford | Stamford | 111 Harbor View Avenue | Sewage Bypass | Dry | 7/16/2021, 6:58 AM | 7/16/2021, 7:09 AM | Treatment Plant | null | Raw Sewage | Mechanical Equipment Failure | Contractor operating an excavator hauling materials accidentally hit an @" automatic vent on temporary 24" HDPE bypass pumping line. | 1,001 - 5,000 gallons | Duration of the leak was determined to be 11 minutes long at an estimated flow of 150 gpm coming out of a 2" nipple. | Estimated to be 1650 gallons | 3000 | Yes | A portion of the flow reached storm drain which flows to Stamford harbor East Branch
Stamford | Stamford | Weed Avenue, Shippan Avenue, Myrtle Avenue, Canal ST. | Sewage Bypass | Rain > 4" per hour | 7/9/2021, 9:34 AM | 7/9/2021, 11:35 AM | Manhole | Unknown at this time | Raw Sewage | Excessive Flows - Storm Event | Via inspections of collection sytem | 501 - 1,000 gallons | Estimated | Unknown | 750 | Yes | Long Island Sound | Various sections of the sanitary sewer collection were observed surcharged due to recent storm event and the on-going construction upgrade activities at the wastewater plant.
Stamford | Stamford | 102 Seaside Ave. | Sewage Bypass | Rain > 4" per hour | 9/1/2021, 11:51 PM | 9/2/2021, 12:50 AM | Lateral - Private | No | Raw Sewage | Excessive Flows - Storm Event | Reported via email to WPCA | Undetermined | Unknown | Unknown | 30 | No |  | Hurricane Ida contributed to excessive precipitation.
Stamford | Stamford | 55 Wardwell ST. | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 2:43 AM | 9/2/2021, 3:21 AM | Lateral - Private | Unknown at this time | Raw Sewage | Excessive Flows - Storm Event | Property owner sent email to WPCA insurance adjuster | Undetermined | Unknown | Unknown | 30 | No
Stamford | Stamford | Pump Station Road and Harbor View Avenue | Sewage Bypass | null | 9/2/2021, 4:38 AM | 9/2/2021, 4:38 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator making rounds. | Over 1,000,000 gallons | Not known | Not known | 1000000 | Yes | East Branch, Stamford Harbor, Long Island Sound | Tropical Storm IDA dumped approximately 7.25" of rain on the City of Stamford. Plant is hydraulically overloaded and mixed liquor is surcharging tanks and entering the storm sewers. Plant discharge flow has been over 72 MGD for the last five hours, surpassing the peak hourly flow of 68 MGD. Secondary treatment has been bypassed with the blowers, recycle pumps, and mixers turned off by approximately 12:00 AM. Primary tank #1 sustained damage and rake assembly turned off.
1048140

## STONINGTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Stonington - Collection System | Stonington | 4 Skipper St., Stonington CT | Sewage Bypass | Rain <1" per hour | 5/30/2021, 2:30 PM | 5/30/2021, 4:45 PM | Pump Station | null | Raw Sewage | Electrical Equipment Failure | Called in by local resident | 501 - 1,000 gallons | Estimated rate of flow from manhole X length of time bypass was occurring | Approx. 1000 gals. or less | 1000 | Yes | Fisher's Island Sound | LOCATION: Boulder Ave. pump station at intersection of Boulder Ave. and Skipper St. Bypass from manhole at the intersection. Bypass was stopped at approx. 4:40 PM, problem at the pump station was corrected.
Stonington - Mystic | Stonington | 175 Whitehall ave | Sewage Bypass | Dry | 3/26/2021, 3:18 PM | 3/26/2021, 4:18 PM | null | No | Raw Sewage | Sewer Line Blockage - Other | Flow meter | 51 - 500 gallons | Average pump run time |  | 300 | No |  | Force main break

## STRATFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Stratford | Stratford | Birdseye street | Sewage Bypass | Dry | 11/18/2021, 11:15 AM | 11/18/2021, 12:00 AM | Treatment Plant | null | None | Electrical Equipment Failure | Equipment Failures | Undetermined |  |  | 10000 | Yes | Housatonic River | One of our substations lost partial power. Electrical engineering company is enroute to diagnose/repair. The only equipment we were unable to restart was the UV disinfection. The discharge is fully treated except for disinfection at this time.
Stratford | Stratford | Beacon Point Rd. | Sewage Bypass | Rain 1-2" per hour | 7/2/2021, 12:30 AM | 7/2/2021, 1:21 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Low UV alarm | 100,001 - 500,000 gallons | SCADA Trend | 227500 | 227500 | Yes | Housatonic River | The discharge was treated up until UV disinfection. Some solids loss contributed to the dosage going below permit for about an hour. Permit requires a minimum of 30 mW s/cm2. UV dose dropped to about 18 mW s/cm2 during that time frame. Adjustments to the process equipment and chemical dosing allowed the plant to return to normal.
Stratford | Stratford | Stratford Ave | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 2:45 PM | 7/9/2021, 8:45 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other | Flooding on roadway | Undetermined |  |  | 300 | Yes | Bruce Brook | The road was dug up to investigate for a break but nothing was found. We believe water had escaped from the joints of the pipe and also the manhole. There is no way to determine flow at that location. The sewer line appears to be broken. We have a contractor scheduled to repair the line.
Stratford | Stratford | Beacon Point Road | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:55 AM | 7/10/2021, 1:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Alarms | Undetermined |  | 20 MG | 20000000 | Yes | Housatonic River | We calculated about 20 MG in a 16 hour time span where the dosage was below permit. We also had solids loss during that time as well. All of our equipment was in service and running and/or available if needed during that time.
Stratford | Stratford | Avery St | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:55 AM | 7/10/2021, 1:00 PM | Sewer Main | null | Raw Sewage | Excessive Flows - Storm Event | Resident called | Undetermined |  |  | 300 | Yes | Housatonic River | The roadway was flooded from the rainwater overflowing from the storm basins which made it difficult to determine how many gallons were discharged from the sewer main.
Stratford | Stratford | Street addresses in comment section | Sewage Bypass | Rain 1-2" per hour | 7/9/2021, 9:55 AM | 7/10/2021, 1:00 PM | Basement | Yes | Raw Sewage | Excessive Flows - Storm Event | Residents called | Undetermined |  |  | 200 | No |  | The excessive flows caused surcharging to occur in several of the sewer mains. As a result, several residents had sewage in their basements. Addresses as follows: 221 Parkwood Pl, 94 Everette St., 1346 Elm St., and 314 Knolton St.
Stratford | Stratford | Beacon Point Road | Sewage Bypass | Rain 1-2" per hour | 9/1/2021, 11:53 PM | 9/1/2021, 11:53 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | UV Dosage alarm | Undetermined |  |  | 7500000 | Yes | Housatonic River
27738300

## SUFFIELD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Suffield | Suffield | 222 Quail Run | Sewage Bypass | null | 10/11/2021, 3:30 PM | 10/11/2021, 5:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Grease | Home Owner | 51 - 500 gallons | Estimate |  | 300 | No |  | Blockage was from grease. Line was cleaned three times. manholes down stream were also checked.
Suffield | Suffield | 480 Hickory Street | Sewage Bypass | Dry | 3/23/2021, 3:04 PM | 3/23/2021, 3:10 PM | Lateral - Private | No | Raw Sewage | Mechanical Equipment Failure | By homeowner | 1-50 gallons | estimate |  | 30 | No |  | Home owner has a grinder pump with a basin, They noticed sewage coming out of the basin. The grinder pump is not working correctly and homeowner is calling a plumber.
Suffield | Suffield | 696 Thrall Ave Suffield | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 4:48 AM | 9/2/2021, 5:55 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Staff checking the service area | 51 - 500 gallons | Visual estimate |  | 300 | No
Suffield | Suffield | 18 Fiddlehead Place Suffield | Sewage Bypass | Dry | 9/20/2021, 5:00 PM | 9/20/2021, 6:30 PM | Manhole | null | Raw Sewage | Mechanical Equipment Failure | Leaking manhole called in by a resident | 1-50 gallons | Only 1 home connected to the manhole, a trickle was coming out making a small wet spot. No standing water. |  | 30 | No |  | The bypass was in a new development with grinder pumps. The contractor who installed the individual home connections onto a manifold pipe in the manhole left the ball valves open that are intended for future connections. There was only 1 home connected to the main and 3 open valves.

## THOMASTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Thomaston WPCF | Thomaston | Old Waterbury rd. | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 3:42 AM | 9/2/2021, 5:30 AM | Treatment Plant | No | Raw Sewage | Excessive Flows - Storm Event | Called in by scada alarm | 1,001 - 5,000 gallons | Current flow |  | 5000 | Yes | Naugatuck river | Lost a primary effluent pump during a heavy rain event. Set up a bypass pump.

## TORRINGTON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
TORRINGTON WPCF | Torrington | 947 New Litchfield St, Torrington, CT | Sewage Bypass | Dry | 12/31/2021, 10:15 AM | 12/31/2021, 10:15 AM | Sewer Main |  | Raw Sewage | Unknown | Torrington fire dept. notified WPCF that sewage was overflowing from a manhole in the grass in front | 200 gallons | guess based on time overflow was first noticed to when we cleared the blockage. The manhole that was |  |  | No
Torrington WPCF | Torrington | 200 kennedy Dr. | Sewage Bypass | Dry | 3/20/2021, 12:53 PM | 3/22/2021, 1:55 PM | Sewer Main | null | Raw Sewage | Unknown | reported by the public | Undetermined | undetermined |  |  | Yes | small stream in back of 200 kennedy Dr. | A member of the public saw sewage coming out of the manhole on a rite of way near a siphon. We immediately cleared blockage and cleaned the area.
Torrington WPCF | Torrington | high st | Sewage Bypass | Dry | 6/28/2021, 12:30 PM | 6/28/2021, 2:03 PM | Sewer Main | null | Raw Sewage | Sewer Line Blockage - Other |  | Undetermined |  |  |  | Yes | naugatuck river
Torrington WPCF | Torrington | 252 Bogue Rd. | Sewage Bypass | Rain <1" per hour | 7/10/2021, 3:48 PM | 7/10/2021, 3:48 PM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Mechanical Equipment Failure | When Staff arrived in the morning | Over 1,000,000 gallons | estimate |  |  | Yes | Naugatuck River | One aeration tank is under construction and due to the rain? high flows the activated sludge back fed into the tank. The only way to drain the tank was to open a drain into the basement where the RAS / WAS pumps are located. This is standard procedure for staff when draining an aeration tank. The sump pumps failed, the alarms did not call out, and the basement flooded with activated sludge making the RAS/WAS pumps fail to run which also did not call out resulting in loss of inventory.
Torrington WPCF | Torrington | Harmon St | Sewage Bypass | Dry | 7/13/2021, 1:55 PM | 7/13/2021, 2:56 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | home owner called | 1-50 gallons | there was a slow trickle coming from the manhole lid. Volume was assesed by looking at the small amount on the road | unknown estimated to be around 10 gallons | 10 | No |  | the sewer main was only partially blocked therefore the amount of spillage was minimal
Torrington WPCF | Torrington | palmer st bridge and scoville st | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 10:45 AM | 9/2/2021, 10:46 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | notice during investigation | Undetermined |  |  | 300 | Yes | naugatuck river
Torrington WPCF | Torrington | Beecher St | Sewage Bypass | Rain 2-3" per hour | 9/2/2021, 10:50 AM | 9/2/2021, 10:52 AM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | high water event investigation | Undetermined |  |  | 300 | Yes | Naugatuck river

## TRUMBULL
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Trumbull WPCA | Trumbull | 6923 Main Street | Sewage Bypass | Dry | 3/9/2021, 1:00 PM | 3/9/2021, 2:30 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Call In | 51 - 500 gallons | Reference Sheet for Estimating Sewer Flow Rate for Overflowing Manholes | Unkown | 300 | No |  | This was an easement coming from condos above easement property stoppage was in the down stream manhole which is a drop, drop pipe was clogged with grease and rags

## UCONN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
University of Connecticut | Mansfield | Horsebarn Hill Road | Sewage Bypass | Dry | 1/3/2021, 5:00 PM | 1/5/2021, 12:00 PM | Sewer Main | No | Raw Sewage | Unknown | Water observed to be bubbling/seeping out of the ground while walking along Horsebarn Hill Road by FacOps employee | 51 - 500 gallons | ~240 gallons |  | 240 | No |  | WPCF and Public Works were notified and further investigated the situation. Pumps were turned on/off and it was determined to be a pipe leak. Suburban Sanitation was contracted to pump down the wet well in the lift station. The repair is scheduled for Tuesday, 1/5.
University of Connecticut | Mansfield | Glenbrook Road | Sewage Bypass | Snowmelt | 2/24/2021, 4:00 PM | 3/23/2021, 4:00 PM | Pump Station | No | None | Other | During the daily inspection, operator noted alarms at the Cogen Lift Station. WPCF was notified and investigated further. A broken/leaking pipe was noted and will be repaired. | 0 | Sewage was contained to the lift station. The lift station was pumped out by Sanitrol today and the Godwin Bypass pumps were installed temporarily until the pipe repair will be complete. | N/A | 0 | No |  | The Godwin bypass pumps are installed at this lift station. Additionally, if needed Sanitrol will be called if the pump station needs to be pumped out.
University of Connecticut | Mansfield | 40 ledoyt road ext | Sewage Bypass | Rain <1" per hour | 7/1/2021, 1:16 PM | 7/1/2021, 1:30 PM | Manhole | null | None | Mechanical Equipment Failure | Alarms through SCADA - Cl2 residual was low checked manholes where pipes run found a leak in the carry line | 0 |  |  | 0 | No |  | This was a leak in a man hole that caused a low residual at the contact chamber was found and repaired temporarily. During a cable pull for plant swcurity upgrades a fiber optic wire was cut.
University of Connecticut | Mansfield | 30 Plains Road | Sewage Bypass | Rain 1-2" per hour | 7/10/2021, 1:15 AM | 7/10/2021, 2:45 AM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | SCADA High Level Alarms | 51 - 500 gallons | Estimate |  | 300 | No |  | Due to the heavy rain even, Storm Elsa.
University of Connecticut | Mansfield | 30 Plains Road | Sewage Bypass | Rain <1" per hour | 7/9/2021, 11:30 AM | 7/9/2021, 2:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | During Rounds and SCADA alarms | 51 - 500 gallons | Estimate |  | 300 | No |  | WPCF operators are closely monitoring SCADA and on-site at the lift station.
University of Connecticut | Mansfield | Horsebarn Hill Road | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 3:30 AM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | SCADA alarm | 51 - 500 gallons | Estimate |  | 300 | No
1140

## US NAVY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
US NAVAL SUB BASE (DEPT OF NAVY) | Groton | 534 Thresher Ave, Groton, CT | Sewage Bypass | Dry | 12/10/2021, 12:45 PM | 12/10/2021, 07:45 PM | Pump Station |  | Raw Sewage | Mechanical Equipment Failure | Visually, wastewater surfaced and puddled on Thresher Avenue, west of Building 534 at sewer lift sta | Unknown | Visually | Unknown | 100 | No |  | PWD responded and determined that a 3" forced sewer main was leaking. FD, EV, PWDO and CBYD notified
US NAVAL SUB BASE (DEPT OF NAVY) | Groton | 1330 Amberjack Rd, Groton, CT | Sewage Bypass | Dry | 12/16/2021, 02:15 PM | 12/16/2021, 02:30 PM | Manhole |  | Raw Sewage | Sewage Line Blockage - Grease | A pedestrian observed the bypass and reported to NSSF Safety & Environmental Department . | 40 gallons | Visual observation | 40 gallons | 40 | No | Bypass did not reach the local waterbody (Thames River). | Sewage reached storm drain approximately 2' from release. Sewage was observed in the adjacent storm
US NAVAL SUB BASE (DEPT OF NAVY) | Groton | 91 Hornbeam Rd, Groton, CT | Sewage Bypass | Rain less than 1" per hour | 12/22/2021, 08:00 AM | 12/22/2021, 02:45 PM | Lateral - Private |  | Raw Sewage | Unknown | Reported by Housing Administrator to Public Work Department. | >100 gallons to ground and storm ditch | Visual | Unable to estimate volume since start time of sewage bypass is unknown. No buildings were impacted. | 100 | No |  | Two (2) sewer manholes covered with undergrowth and soil were located behind 91 Hornbeam Rd. Underg

## VERNON
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Dry | 1/22/2021, 12:25 PM | 1/22/2021, 1:00 PM | Treatment Plant | No | None | Approved Bypass for Construction | Bypass was initiated | 20,001 - 50,000 gallons | Influent flow meter | 24290 |  | Yes | Hockanum River | This was a test of an approved bypass of secondary effluent/treated wastewater for construction activities.
Vernon WPCF | Vernon | 100 Windsorville Road Vernon CT | Sewage Bypass | Dry | 1/25/2021, 8:00 AM | 1/29/2021, 2:45 PM | Treatment Plant | No | None | Approved Bypass for Construction | Bypass was initiated | Undetermined | Influent flow meter | 16380000 gallons |  | Yes | Hockanum River | This is an approved bypass of secondary effluent/treated wastewater for construction activities.
Vernon WPCF | Vernon | 100 Windsorville Road Vernon CT | Sewage Bypass | Dry | 10/1/2021, 9:20 AM | 10/1/2021, 2:45 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Contractor notified plant employees | Undetermined | N/A | Unknown |  | Yes | Hockanum River | Bypass is disinfected secondary effluent. Partial phosphorous removal at this time. Contractor is working on controls for intermediate pumps and having difficulty resolving issue with faulting VFD's.
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Dry | 11/4/2021, 3:30 AM | 11/4/2021, 4:36 AM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Security guard noticed water coming out of intermediate wet well | 100,001 - 500,000 gallons | Influent Flow Meter | 114,510 gallons |  | Yes | Hockanum River | Bypass was secondary influent coming from intermediate wet well. Controls for intermediate pumps turned off for unknown reason which stopped the pumps from pumping to the filter building and allowed the well to overflow. Engineer will be here this morning to determine what happened and correct the issue.
Vernon WPCF | Vernon | 85 Peterson Road Vernon | Sewage Bypass | Dry | 5/6/2021, 7:30 PM | 5/6/2021, 8:00 PM | Sewer Main | Yes | Raw Sewage | Sewer Line Blockage - Grease | Sewage Coming Out of Manhole | 1-50 gallons | Estimate/Visual |  |  | No |  | Blockage in main sewer line backed up sewage into home and out manhole in street.
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Dry | 6/20/2021, 7:00 AM | 6/20/2021, 7:05 AM | Treatment Plant | No | None | Electrical Equipment Failure | Operator came in for his scheduled 4 hour shift | 100,001 - 500,000 gallons | Flow measurement at time of electrical failure | 368000 |  | Yes | Hockanum River | Type of bypass is secondary treated effluent. VFD's faulted for intermediate pumps which pumps secondary effluent to filter building. Intermediate well overflowed to catch basin which discharges to Hockanum River. When operator arrived, he initiated the bypass of the flow from the intermediate wet well directly to the UV channel.
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Rain 1-2" per hour | 7/17/2021, 6:20 PM | 7/20/2021, 1:00 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Monitoring intermediate pump wet well level and pump speed | Undetermined |  |  |  | Yes | Hockanum River | Bypass is secondary clarifier effluent. All flows are being disinfected by UV. Flows off of secondary clarifiers are pumped by intermediate pump to filter building for phosphorous treatment. One duty pump was put into service to accommodate typical flows with 12 MGD maximum capacity. Flows due to rain exceeded 12 MGD so bypass was partially opened to bleed off excess flow to UV channel, pump speed running 100% and still treating phosphorous. Waiting for flows to subside below 12 MGD to close.
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Rain <1" per hour | 7/9/2021, 11:30 AM | 7/12/2021, 3:00 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator monitoring intermediate wet well level and pump speed | Undetermined |  |  | 1000000 | Yes | Hockanum River | Bypass is secondary clarifier effluent. All flows are being disinfected by UV. Flows off of secondary clarifiers are pumped by intermediate pump to filter building for phosphorous treatment. One duty pump was put in service to accommodate typical flows with 12 MGD maximum capacity. Flows due to rain exceeded 12 MGD so bypass was partially opened to bleed off excess flow to UV channel, pump running at 100% and still treating for phosphorous. Waiting for flows to subside below 12 MGD to close.
Vernon WPCF | Vernon | 100 Windsorville Road | Sewage Bypass | Rain 1-2" per hour | 8/22/2021, 2:40 PM | 8/24/2021, 1:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator onsite monitoring flows, initiated partial bypass of tertiary phosphorous treatment | Undetermined |  |  | 1000000 | Yes | Hockanum River | Bypass is secondary effluent that is UV disinfected prior to discharge to river. Partial bypass of tertiary phosphorous treatment due to excessive flows from Tropical Storm Henri .
Vernon WPCF | Vernon | 100 Windsorville Road Vernon | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 1:40 AM | 9/6/2021, 11:30 PM | Treatment Plant | No | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operator Monitoring Flows | Undetermined |  |  | 1000000 | Yes | Hockanum River | Partial bypass is disinfected secondary effluent from tertiary phosphorous removal. All flows are disinfected by UV.

## WALLINGFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Wallingford | Wallingford | 155 John Street, Wallingford CT 06492 | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 10:30 AM | 7/9/2021, 3:00 PM | Treatment Plant | No | Raw Sewage | Excessive Flows - Storm Event | Overflowing Preliminary Treatment | Over 1,000,000 gallons | Estimated Flow by hours bypass |  | 1000000 | Yes | Quinnipiac River
Wallingford | Wallingford | 225 Pond Hill Road, Wallingford CT 06492 | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 11:45 PM | 7/10/2021, 12:40 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | Sewage overflowing out of manhole | 20,001 - 50,000 gallons | Calculated Estimate |  | 30000 | No
Wallingford | Wallingford | south Elm St | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 3:00 PM | 9/2/2021, 3:10 PM | Manhole | No | Raw Sewage | Excessive Flows - Storm Event | reported | 501 - 1,000 gallons | estimate |  | 3000 | No
Wallingford | Wallingford | 155 John St | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 4:00 AM | 9/2/2021, 8:00 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | operators | Over 1,000,000 gallons | estimate |  | 1000000 | Yes | quinnipiac river
2033000

## WATERBURY
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Waterbury WPCF | Waterbury | 52 Terrell Road, Waterbury, CT 06708 | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 12:46 AM | 9/2/2021, 1:15 AM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | SCADA Alarm | 501 - 1,000 gallons | By reference sheet for estimating sewer spills approximately 750 gallons of raw sewage (25 gpm for 30 minutes | 750 | 750 | No | N/A | On 9/2/21, Terrell Rd pump station experienced abnormal high flows caused by Tropical Storm Ida. At 12:46 am, the pumps at the station could not keep up with the flow so the canned station flowed and sewage was spilled out of pump station manhole. The collections Team used vactor trucks to vacuum the station, the manhole, and the area around. Bypass was stopped at 1:15 am on 9/2/21. The station was then maintained by vactor trucks until rain subsided.
Waterbury WPCF | Waterbury | 210 Municipal Road, Waterbury CT 06708 | Sewage Bypass | Rain 1-2" per hour | 9/2/2021, 12:02 AM | 9/2/2021, 5:30 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | SCADA influent flow meter | Undetermined | N/A | Unknown | 1000000 | Yes | Naugatuck River | As referenced on the Emergency Response Plan for Plant Bypasses, the WPCF is designed to fully treat flows of up to 50.3 MDG and partially treat up to an additional 33.9 MGD (using primary treatment, but bypassing secondary treatment) with the partially treated flows disinfected prior to discharging to the Naugatuck River. Flows in excess of 84.2 MGD cannot be treated or disinfected by the Plant and these excess flows must be diverted directly to the River.
Waterbury WPCF | Waterbury | 62 Laval Street | Sewage Bypass | Dry | 4/4/2021, 9:43 AM | 4/4/2021, 12:00 AM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | City of Waterbury Health Dept. Called in complaint from homeowner | 51 - 500 gallons | Visual | 100 gal | 100 | No |  | Investigated downstream manhole in front of 62 Laval Street. Found manhole to be surging. Jetted line to clear blockage. Inspected house basement and found backup coming form sump in basement which acts as a floor drain to sanitary sewer line.
Waterbury WPCF | Waterbury | 60 Decicco Road, Waterbury, CT | Sewage Bypass | Dry | 11/16/2021, 2:10 PM | 11/16/2021, 2:55 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | home owner | 1-50 gallons | visual | 1-50 gallons | 30 | No |  | Date and time bypass began was 11/14/2021 at 2:10 PM and Date and time bypass ended was 11/14/2021 at 2:55 PM
Waterbury WPCF | Waterbury | 88 Lakeview Drive, Waterbury | Sewage Bypass | Dry | 1/14/2021, 1:45 PM | 1/14/2021, 2:50 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Resident called in to sewer department | 1,001 - 5,000 gallons | Used SSO IMD.Nov 2010 Appendix H Was to estimate SSO volume | 4,400 gallons | 4400 | Yes | Mad river | Dispatched jetter-vac truck and released blockage and by-pass by 2:50 pm
Waterbury WPCF | Waterbury | 23 Commercial Street, Waterbury CT | Sewage Bypass | Dry | 2/25/2021, 11:40 AM | 2/25/2021, 1:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Resident call customer service | 1,001 - 5,000 gallons | puddle volume (dimensions of the parking lot, average depth) | 3485 | 3485 | No | N/A | Bypass was stopped at 1:00 pm. Cleaning activities were performed so the majority of the spill was recovered with vactor trucks
Waterbury WPCF | Waterbury | 38 Hobart Street | Sewage Bypass | Dry | 5/24/2021, 9:52 AM | 5/24/2021, 11:15 AM | Manhole | Yes | Raw Sewage | Sewer Line Blockage - Other | Homeowner called in backup | 51 - 500 gallons | Visual | 100 gallons | 100 | No |  | Manhole in street surging and releasing small amount of sewage on street. Minimal backup in residence basement from washing machine drain
Waterbury WPCF | Waterbury | 250 Northridge Drive, Waterbury CT | Sewage Bypass | Other | 2/18/2021, 7:55 AM | 2/18/2021, 8:05 AM | Pump Station | null | Raw Sewage | Sewer Line Blockage - Other | Collections Operator performing maintenance inspection | Undetermined | Pump rate, force main capacity, time | 476 | 476 | No |  | Bypass is stopped. Pumps were shutdown at the station and the wet well is maintained by vactor trucks
Waterbury WPCF | Waterbury | 464 Reidville Drive, waterbury | Sewage Bypass | Dry | 1/1/2021, 10:50 AM | 1/1/2021, 12:30 PM | Sewer Main | No | Raw Sewage | Sewer Line Blockage - Other | City of Waterbury Water Dept. employee called Water Pollution Control | 501 - 1,000 gallons | Visual | less than 1000 gallons | 950 | Yes | Mad River | Sewer line blockage caused by broken manhole cover in manhole. Broken cover removed, blockage cleared and line jetted clean. Replaced cover and manhole functioning normal
Waterbury WPCF | Waterbury | 300 Schraffts Drive, Waterbury, CT | Sewage Bypass | Dry | 10/1/2021, 2:47 PM | 10/2/2021, 9:30 AM | Lateral - Private | No | Raw Sewage | Sewer Line Blockage - Roots | Received call by from Citizen | Undetermined | undetermined | undetermined | 20 | No |  | The time that the bypass began was 12:20 PM on 10-1-21. According to the Health Department the blockage was released by American Rooter on Saturday, 10-2-21 at about 9:30 am
Waterbury WPCF | Waterbury | 460 Farmington Avenue | Sewage Bypass | Dry | 10/12/2021, 2:35 PM | 10/17/2021, 2:35 PM | Lateral - Private | No | Raw Sewage | Unknown | Resident called customer service | 1-50 gallons | Private issue - volume could not be estimated | Unknown | 20 | No | N/A | Private issue - curb box discharging. Health Department was informed of the issue.
Waterbury WPCF | Waterbury | 439 Piedmont St, Waterbury CT 06706 | Sewage Bypass | Rain <1" per hour | 10/26/2021, 12:30 PM | 10/27/2021, 12:30 PM | Lateral - Private | No | Raw Sewage | Unknown | Waterbury's Department of Public Health | 1-50 gallons | measures of the spill area | 100 | 30 | No | N/A | Waterbury's Department of Public Health (DPH) indicated that the owner/resident of 439 Piedmont St was pumping sewage into his backyard. The sewer line and manholes his lateral is connected to were inspected and no issues or blockage were found. DPH called private contractor and the blockage in the lateral was cleared on 10/27/21
Waterbury WPCF | Waterbury | 52 Clairmont Avenue, Waterbury, CT | Sewage Bypass | Dry | 11/2/2021, 3:52 PM | 11/3/2021, 9:10 AM | Lateral - Private | No | Raw Sewage | Unknown | Richard Lee from Health Department | 1-50 gallons | visual |  | 30 | No |  | This is private lateral issue that has been referred to the Health Department.DPH said they sent Inspector Harvey, who contacted landlord regarding the sewage bypass and the landlord hired Klear Klogs Sewer & Drain Cleaning to clear the blockage on November 2. The DH Inspector conducted re-inspection on November 3 at around 9:10 am and confirmed that the sewage bypass was resolved.
WATERBURY WPCF | Waterbury | 1746 E Main St, Waterbury, CT | Sewage Bypass | Dry | 12/2/2021, 08:45 AM | 12/2/2021, 09:15 AM | Lateral - Private |  | Raw Sewage | Unknown | Notification from Melvin Santiago | 1-50 gallons | visual | 1-50 gallons | 30 | No |  | Refer to Waterbury Health Department
WATERBURY WPCF | Waterbury | 57 River St, Waterbury, CT | Sewage Bypass | Dry | 12/3/2021, 02:30 PM | 12/6/2021, 10:00 AM | Lateral - Private |  | Raw Sewage | Unknown | Complaint from Jose Acosta | 1-50 gallons | Visual - signs of discharge | 30 gallons | 30 | No |  | Heath Department inspector contacted landlord regarding the sewage bypass and the landlord told the
1010451

## WATERFORD
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
Waterford | Waterford | Magonk Point Road | Sewage Bypass | Dry | 8/31/2021, 11:56 AM | 9/1/2021, 1:00 AM | Pump Station | null | Raw Sewage | Mechanical Equipment Failure | Neighbor call. | 51 - 500 gallons | Estimated |  | 300 | No |  | A wet area was noted near the location of the Seaside PS 8-inch force main . Neighbor called office. The force main was drained back to the PS. Tankers were used to by-pass the station. The Seaside PS is a relatively small PS. Staff and contractors were used to repair the pipe. The repair was completed about 1:00 am on Sept. 1. Trench backfilled. Station back in service after repair completed.
Waterford | Waterford | Cross Road, Waterford, CT | Sewage Bypass | Dry | 9/27/2021, 2:00 PM | 9/26/2021, 2:20 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | Adjacent property manager | 51 - 500 gallons | Visual estimate based on wet area | unknown | 300 | No | N/A | A spill out a manhole located on a large grass area outside BJs in Waterford was reported by BJs property manager. Our crew immediately mobilized, cleared the backup, and cleaned the pipe. It appears that non-flushable materials are being discharged into the collection system.

## WEST HAVEN
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | DEEP ESTIMATE FOR REPORT | Reach Waterbody? | Waterbody Name | Comments
West Haven | West Haven | Painter Drive | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 12:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | pump station couldnot keep up with the water | 5,001 - 20,000 gallons |  |  | 10000 | Yes | Cove River | Cove River Pump Station
West Haven | West Haven | 183 bull hill ln | Sewage Bypass | Dry | 10/2/2021, 2:10 PM | 10/2/2021, 3:00 PM | Manhole | Yes | Raw Sewage | Sewer Line Blockage - Grease | homeowners | 1-50 gallons | visual |  | 20 | Yes | drainage culvert | mh #9-5 and mh#9-4
West Haven | West Haven | Dawson Avenue/Ocean Avenue | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 12:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | pump station could not keep up with the water flow | 5,001 - 20,000 gallons |  |  | 10000 | Yes | Long Island Sound | Dawson Avenue Pump Station
West Haven | West Haven | Blohm Street | Sewage Bypass | Rain > 4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 12:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | pump station could not keep up with water flow | 5,001 - 20,000 gallons |  |  | 10000 | Yes | Long Island Sound | Main Pump Station
West Haven | West Haven | Beach Street | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:08 AM | 9/2/2021, 2:08 AM | Treatment Plant | null | Raw Sewage | Excessive Flows - Storm Event | employees here at the plant | 5,001 - 20,000 gallons |  |  | 10000 | Yes | Long Island Sound | Water Pollution Control Treatment Plant
West Haven | West Haven | 171 beatrice avenue | Sewage Bypass | Rain 3-4" per hour | 7/9/2021, 9:14 AM | 7/9/2021, 11:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event |  | 1,001 - 5,000 gallons |  |  | 2000 | Yes | new haven harbor | multiple pump station down due to heavy rain from tropical storm elsa dawson avenue, Oyster River, front ave ,morrissy ln, main pump station blohm st, cove river station,savin ave station, trumbull st station.
West Haven | West Haven | 2 Beach Street | Sewage Bypass | Rain 2-3" per hour | 7/9/2021, 9:20 AM | 7/9/2021, 10:55 AM | Treatment Plant | null | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Operations | Undetermined | Plant flows in excess of 20 MGD |  | 1000000 | Yes | New Haven Harbor
West Haven | West Haven | Beatrice Drive | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:00 AM | 9/2/2021, 12:00 PM | Pump Station | Yes | Raw Sewage | Excessive Flows - Storm Event | pump station could not keep up with water flow | 5,001 - 20,000 gallons |  |  | 10000 | Yes | Oyster River | Oyster River Pump Station
West Haven | West Haven | Front Avenue | Sewage Bypass | Rain 3-4" per hour | 9/2/2021, 2:02 AM | 9/2/2021, 12:00 PM | Pump Station | null | Raw Sewage | Excessive Flows - Storm Event | pump station could not keep up with water | 5,001 - 20,000 gallons |  |  | 10000 | Yes | West River | Front Avenue Pump Station
West Haven | West Haven | 101 boston post rd | Sewage Bypass | Dry | 1/10/2021, 1:30 PM | 1/10/2021, 2:00 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | ers | 1-50 gallons |  |  | 20 | Yes | west river | heavy linens from a linen facility discharging linens into line.
West Haven | West Haven | 103 orange ave | Sewage Bypass | Dry | 3/16/2021, 3:30 PM | 3/16/2021, 4:00 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | resident | 1-50 gallons | visual |  | 20 | Yes | west river
West Haven | West Haven | 44 morrissey ln | Sewage Bypass | Dry | 7/16/2021, 6:29 AM | 7/16/2021, 7:00 AM | Manhole | No | Raw Sewage | Mechanical Equipment Failure | homeowner | 1-50 gallons | visual |  | 20 | No |  | both pumps at lift stations tripped off and needed to be reset.
West Haven | West Haven | 30 Cove Brook Rd. | Sewage Bypass | Dry | 1/20/2021, 4:10 PM | 1/20/2021, 5:15 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Phone Call | 1-50 gallons | Visually | 5 | 5 | No
West Haven | West Haven | 32 eileen st west haven ct 06516 | Sewage Bypass | Dry | 1/22/2021, 2:00 PM | 1/22/2021, 2:33 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | homeowner | 1-50 gallons | visual |  | 20 | No
West Haven | West Haven | 20 tile st westhaven ct 06516 | Sewage Bypass | Dry | 1/8/2021, 10:00 PM | 1/8/2021, 10:40 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | homeowner | 1-50 gallons | homeowner |  | 20 | No
West Haven | West Haven | 28 Zegmont St. | Sewage Bypass | Dry | 2/14/2021, 1:00 PM | 2/14/2021, 1:43 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | Phone call | 1-50 gallons | visually |  | 20 | No
West Haven | West Haven | 128 Winslow Dr. | Sewage Bypass | Dry | 2/15/2021, 3:45 PM | 2/15/2021, 4:15 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | phone call | 1-50 gallons | Visually |  | 20 | No |  | Service Master called
West Haven | West Haven | 89 homeside ave westhaven ct 06516 | Sewage Bypass | Dry | 3/13/2021, 6:15 PM | 3/13/2021, 6:40 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Grease | homeowner | 1-50 gallons |  |  | 20 | No |  | sewage also boiled out of a manhole in same addresses yard approx 10 gallons
West Haven | West Haven | 440 old melody rd | Sewage Bypass | Dry | 3/6/2021, 11:00 AM | 3/6/2021, 11:30 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | Homeowner | 1-50 gallons | Visual |  | 20 | No
West Haven | West Haven | 580 washington ave west haven ct 06516 | Sewage Bypass | Dry | 4/18/2021, 6:30 PM | 4/18/2021, 7:00 PM | Basement | null | Raw Sewage | Sewer Line Blockage - Grease | homeowner | 1-50 gallons | visual |  | 20 | No
West Haven | West Haven | 460 elm st west haven ct | Sewage Bypass | Dry | 5/17/2021, 8:30 PM | 5/18/2021, 9:50 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Grease | building managment | 1-50 gallons | visual |  | 20 | No |  | this bypass is the results of stop and shops separator in the back parking lot. it bypassed from there separator covers and was plugged in there systems line right before it connects to the wpc maim line . bypass is responsibility of the property owner. the city of west haven wpca jetted the blockage and relieved the backup to resolve the issue. pin on map is dropped at location of manhole where bypass occured.
West Haven | West Haven | 57 sanford st/ 31 sanford st | Sewage Bypass | Dry | 7/15/2021, 5:00 PM | 7/15/2021, 5:30 PM | Sewer Main | Yes | Raw Sewage | Sewer Line Blockage - Grease | homeowner and police | 1-50 gallons | visual |  | 20 | No |  | manhole id# 13-66 bypassed and also address #31 sanford bypassed small amount less then 10 gallons in basement .
West Haven | West Haven | 255 blohm st west haven ct 06516 | Sewage Bypass | Dry | 1/6/2021, 11:00 AM | 1/6/2021, 11:39 AM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | homeowner | 1-50 gallons | visual |  | 20 | No
West Haven | West Haven | 102 hillside st west haven ct | Sewage Bypass | Dry | 3/14/2021, 12:00 PM | 3/14/2021, 12:45 PM | Manhole | No | Raw Sewage | Sewer Line Blockage - Other | police | 1-50 gallons | visual |  | 20 | No |  | someone threw a piece of pipe into manhole plugging the invert
West Haven | West Haven | 65 jones hill rd | Sewage Bypass | Dry | 8/29/2021, 9:00 PM | 8/29/2021, 9:40 PM | Basement | Yes | Raw Sewage | Sewer Line Blockage - Other | homeowner | 1-50 gallons | visual |  | 20 | No
West Haven | West Haven | 13 thill st | Sewage Bypass | Dry | 4/19/2021, 10:20 AM | 4/19/2021, 11:21 AM | Manhole | Yes | Raw Sewage | Sewer Line Blockage - Roots | Homeowner | 1-50 gallons | Visual |  | 20 | No
West Haven | West Haven | Morse ave | Sewage Bypass | Dry | 4/17/2021, 2:24 PM | 4/17/2021, 3:00 PM | Sewer Main | null | Raw Sewage | Unknown | Homeowner | 1-50 gallons | Visual |  | 20 | No
1062365

## WESTPORT
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Westport | Westport | 25 Crescent Road, Cross Street is Crescent Park Road | Sewage Bypass | Rain > 4" per hour | 7/9/2021, 2:30 PM | 7/9/2021, 5:00 PM | Manhole | null | Raw Sewage | Excessive Flows - Storm Event | Resident Called | 1,001 - 5,000 gallons | Based on flow from manhole | < 5,000 | No |  | Pumping it down Received over 6" of rain

## WINDSOR LOCKS
Utility | Town | Closest Street Address | Incident Type | Weather Conditions | Bypass Began or Discovered | Bypass Ended | Location | Sewer Main Blockage | Type of Bypass | Cause of Bypass | How was event discovered? | Estimate Quantity or Volume | Quantity or Volume determined | Final Volume | Reach Waterbody? | Waterbody Name | Comments
Windsor Locks WPCF | Windsor Locks | Stanton Road | Sewage Bypass | Other | 7/19/2021, 6:15 AM | 7/19/2021, 1:30 PM | Manhole | null | Raw Sewage | Sewer Line Blockage - Other | Alarm at plant for Influent Wet Well High Level call out | 51 - 500 gallons | Guestimate of area of sewage around manhole |  | No | Connecticut River | Sewage around manhole area raked up and disposed of in grit container. Put lime down on area.